## SD C
SHUTDOWN OF COMPRESSOR C EFFECTS CAUSE | [7 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[8 empty] | EQUIP. | C-2101 / C-2102
[8 empty] | EFFECT | FEED BACK ESD | FEED BACK ESD | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | SPILL BACK SV | MAIN MOTOR STOP | AUX. OIL PUMP START | AUX. OIL PUMP STOP | CRANCK CASE HEATER OFF | AUX. WATER PUMP STOP | MAIN WATER PUMP STOP | WATER RESERVOIR HEATER STOP | LUBRICATOR PUMP STOP | COMMON SHUT DOWN LAMP LCP | LUBRICATOR HEATER STOP | LUBE OIL COOLER MOTOR A STOP | LUBE OIL COOLER MOTOR B STOP | COOLING WATER COOLER MOTOR A STOP | COOLING WATER COOLER MOTOR B STOP
[8 empty] | TAG NO. | ESD2A-C-2101-C | ESD2-C-2101-C | PSOV-2201C | PSOV-2202C | PSOV-2203C | PSOV-2204C | PSOV-2205C | PSOV-2123C | XSP-2200C | XSS-2202C | XSP-2202C (NOTE 2) | XSP-2203C | XSP-2221C | XSP-2222C | XSP-2223C | XSP-2201C (NOTE 2) | ESDL-2245C | XSP-2200C | XSP-2205C | XSP-2206C | XSP-2220C | XSP-2226C
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | TRIP RELAY CENTER (NOTE 4) | INTERLOCK NO. | LOCATION | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | LCP 2101C | MCC | MCC | MCC | MCC | MCC
SOUR GAS RECIPROCATING COMPRESSOR | C-2101 / C-2102 | ESDR2A-C-2101-C | BK-GCS-HY-120-IN-DW-0006 | 9C of 10 | CLIENT ESD SIGNAL | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | ESDR2-C-2101-C | BK-GCS-HY-120-IN-DW-0006 | 9C of 10 | CLIENT ESD SIGNAL | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | ESD-2231 C | BK-GCS-HY-120-IN-DW-0006 | 9C of 10 | EMERGENCY SHUTDOWN PUSH BUTTON ON UCP | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | ESD-2245 C | BK-GCS-HY-120-IN-DW-0006 | 8C of 10 | EMERGENCY SHUTDOWN PUSH BUTTON ON LCP | USD | I-60C | LCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TS-2191 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 1ST STAGE DISCHARGE TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TS-2194 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 2ND STAGE DISCHARGE TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | PS-2133 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 2ND STAGE DISCHARGE LINE PRESSURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | PS-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL PRESSURE LOW LOW | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | PS-2220 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER LINE PRESSURE LOW LOW | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2221 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | VT-2200 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | VT-2201 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | VT-2202 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | COMPRESSOR FRAM VIBRATION HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2216 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | BEARING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2217 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | PACKING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2218 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | BEARING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2220 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MID BEARING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2219 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | PACKING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2214 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR NDE BEARING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TT-2215 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR DE BEARING TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TE-2222 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR WINDING W TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TE-2225 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR WINDING V TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
|  | TE-2228 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR WINDING U TEMPERATURE HIGH HIGH | USD | I-60C | UCP 2101C | T | T | C | C | C | C | O | C | T | S | T | T | T | T | T | T | S | T | T | T | T | T
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER |  |  |  | S: START SP: STOP T: TRIP O: OPEN C: CLOSE |  |  | NOTE 1: THE START PERMISSIVE REQUEST FROM UCP TO DCS, START PERMISSION OF UCP, AND START SEQUENCE (AUTOMATICALLY) SHALL BE CONSIDERED WHEN THE COMPRESSOR START IS FROM UCP. NOTE 2: DURING THE COMPRESSOR STOP, WILL BE STOPPED WITH DELAY TIME. NOTE 3: BEFORE STARTING THE COMPRESSOR FROM LCP, PREHEATING AND PRELUBRICATION STEPS (DISCUSSED IN CONTROL PHILOSOPHY"BK-GCS-HY-120-PR-PH-0001") SHALL BE DONE BY OPERATOR VIA LCP. NOTE4: RELAY TRIP CENTER IS BACK UP OF PLC.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V04
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 11 از 14
CAUSE AND EFFECT CHARTS LIST

## Alarm C
ALARM SIGNALS OF COMPRESSOR C EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C2101 / C-2102
[7 empty] | EFFECT | COMMON ALARM LAMP LCP
[7 empty] | TAG NO. | XF-2245C
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | LCP 2101C
SOUR GAS RECIPROCATING COMPRESSOR | C2101 / C-2102 | PDT-2122 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 1ST STAGE SUCTION STRAINER DIFFRENTIAL PRESSURE HIGH |  | UCP 2101C | S
|  | PT-2123 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 1ST STAGE SUCTION PRESSURE HIGH |  | UCP 2101C | S
|  | TT-2191 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 1ST STAGE DISCHARGE TEMPERATURE HIGH |  | UCP 2101C | S
|  | PT-2124 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 1ST STAGE DISCHARGE PRESSURE HIGH |  | UCP 2101C | S
|  | PT-2132 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 2ND STAGE SUCTION PRESSURE LOW |  | UCP 2101C | S
|  | TT-2194 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 2ND STAGE DISCHARGE TEMPERATURE HIGH |  | UCP 2101C | S
|  | PT-2133 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 2ND STAGE DISCHARGE PRESSURE HIGH |  | UCP 2101C | S
|  | PT-2200 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUBRICATOR PRESSURE LOW |  | UCP 2101C | S
|  | PDT-2132 C | BK-GCS-HY-120-IN-DW-0006 | 1C of 10 | 2ND STAGE SUCTION STRAINER DIFFRENTIAL PRESSURE HIGH |  | UCP 2101C | S
|  | LT-2200 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | CRANK CASE LUBE OIL LEVEL LOW |  | UCP 2101C | S
|  | PDT-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL FILTER DIFFERENTIAL PRESSURE HIGH |  | UCP 2101C | S
|  | PT-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL PRESSURE LOW |  | UCP 2101C | S
|  | TT-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL TEMPERATURE LOW |  | UCP 2101C | S
|  | PT-2210 C | BK-GCS-HY-120-IN-DW-0006 | 4C of 10 | N2 STREAM PRESSURE LOW |  | UCP 2101C | S
|  | PT-2211 C | BK-GCS-HY-120-IN-DW-0006 | 4C of 10 | N2 STREAM PRESSURE LOW |  | UCP 2101C | S
|  | PT-2212 C | BK-GCS-HY-120-IN-DW-0006 | 4C of 10 | N2 PURGE PRESSURE HIGH |  | UCP 2101C | S
|  | LT-2213 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER RESERVOIR LEVEL LOW |  | UCP 2101C | S
|  | PT-2220 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER PRESSURE LOW |  | UCP 2101C | S
|  | PT-2220 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER PRESSURE HIGH |  | UCP 2101C | S
|  | TT-2221 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER TEMPERATURE LOW |  | UCP 2101C | S
|  | TT-2221 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2214 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR NDE BEARING TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2215 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR DE BEARING TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2216 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | BEARING TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2217 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | PACKING TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2218 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | BEARING TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2219 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | PACKING TEMPERATURE HIGH |  | UCP 2101C | S
|  | TT-2220 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MID BEARING TEMPERATURE HIGH |  | UCP 2101C | S
|  | ZT-2200 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | 1ST STAGE ROD DROP HIGH |  | UCP 2101C | S
|  | ZT-2201 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | 2ND STAGE ROD DROP HIGH |  | UCP 2101C | S
|  | VT-2200 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | FRAME VIBRATION HIGH |  | UCP 2101C | S
|  | VT-2201 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | FRAME VIBRATION HIGH |  | UCP 2101C | S
|  | VT-2202 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | FRAME VIBRATION HIGH |  | UCP 2101C | S
|  | TE-2222 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR WINDING W TEMPERATURE HIGH |  | UCP 2101C | S
|  | TE-2225 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR WINDING V TEMPERATURE HIGH |  | UCP 2101C | S
|  | TE-2228 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | MAIN MOTOR WINDING U TEMPERATURE HIGH |  | UCP 2101C | S
|  | XT-2200 C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | KEY PHASOR ROTATION SPEED HIGH |  | UCP 2101C | S
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER |  |  |  | S: START SP: STOP T: TRIP O: OPEN C: CLOSE
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V04
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 12 از 14
CAUSE AND EFFECT CHARTS LIST

## Start permission C
ALARM SIGNALS OF COMPRESSOR C EFFECTS CAUSE
[7 empty] | EFFECT | READY TO START | REQUEST START PERMISSION | COMPRESSOR START PERMISSION LAMP
[7 empty] | TAG NO. | XSS-2124C | XSS-2126C | XSP-2245 C
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | UCP 2101C | UCP 2101C | LCP 2101C
SOUR GAS RECIPROCATING COMPRESSOR | C2101 / C-2102 | XF-2245C | BK-GCS-HY-120-IN-DW-0006 | 8C of 10 | NO COMMON ALARM (LAMP OFF) | I-65C | LCP 2101 C | S | S | S
|  | ESDL-2245C | BK-GCS-HY-120-IN-DW-0006 | 8C of 10 | NO COMMON SHUTDOWN (LAMP OFF) |  | LCP 2101 C | S | S | S
|  | XR-2202C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | AXU. OIL PUMP MOTOR RUN FEED BACK |  | LCP 2101 C | S | S | S
|  | PT-2204C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUBE OIL PRESSURE |  | UCP 2101 C | S | S | S
|  | TT-2204C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUBE OIL TEMPERATURE |  | UCP 2101 C | S | S | S
|  | PT-2220C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER PRESSURE |  | UCP 2101 C | S | S | S
|  | TT-2221C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER TEMPERATURE |  | UCP 2101 C | S | S | S
|  | XZSO-2225C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | BARING DEVICE UNLOCK FEED BACK (ON) |  | UCP 2101 C | S | S | S
|  | XF-2200C | BK-GCS-HY-120-IN-DW-0006 | 7C of 10 | NO MAIN MOTOR FAULT |  | UCP 2101 C | S | S | S
|  | PT-2210C | BK-GCS-HY-120-IN-DW-0006 | 4C of 10 | PRESSURE PACKING N2 PRESSURE |  | UCP 2101 C | S | S | S
|  | PT-2211C | BK-GCS-HY-120-IN-DW-0006 | 4C of 10 | ROD PACKING N2 PRESSURE |  | UCP 2101 C | S | S | S
|  | LT-2200C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUBE OIL LEVEL |  | UCP 2101 C | S | S | S
|  | HSL-2242C1 | BK-GCS-HY-120-IN-DW-0006 | 2C of 10 | CAPACITY SWITCH ON 0% LOAD |  | UCP 2101 C | S | S | S
|  | XSS-2123C | BK-GCS-HY-120-IN-DW-0006 | 9C of 10 | CLIENT PERMISSIVE TO START (NOTE 1) |  | UCP 2101 C | S | S | S
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER |  |  |  | S: START SP: STOP T: TRIP O: OPEN C: CLOSE |  | NOTE 1: A REQUEST PERMISSION SIGNAL (XSS-2126C) FROM UCP WILL BE SENT TO DCS, THEN START PERMISSIOM SIGNAL (HSS-2125C) FROM DCS WILL BE SENT TO UCP.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V04
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 13 از 14
CAUSE AND EFFECT CHARTS LIST

## Control C
START AND CONTROL SIGNALS OF COMPRESSOR C EFFECTS CAUSE | [6 empty] | TITLE | SOUR GAS RECIPROCATING COMPRESSOR
[7 empty] | EQUIP. | C-2101 / C-2102
[7 empty] | EFFECT | FEED BACK ESD | FEED BACK ESD | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | INSTRUMENT AIR | SPILL BACK SV | MAIN MOTOR START | MAIN MOTOR STOP | AUX. OIL PUMP START | AUX. OIL PUMP STOP | CRANCK CASE HEATER ON | CRANCK CASE HEATER OFF | AUX. WATER PUMP START | AUX. WATER PUMP STOP | MAIN WATER PUMP START | MAIN WATER PUMP STOP | WATER RESERVOIR HEATER START | WATER RESERVOIR HEATER STOP | LUBRICATOR PUMP START | LUBRICATOR PUMP STOP | COMMON SHUT DOWN LAMP LCP | LUBRICATOR HEATER START | LUBRICATOR HEATER STOP | LUBE OIL COOLER MOTOR A START | LUBE OIL COOLER MOTOR B START | LUBE OIL COOLER MOTOR A STOP | LUBE OIL COOLER MOTOR B STOP | COOLING WATER COOLER MOTOR A START | COOLING WATER COOLER MOTOR B START | COOLING WATER COOLER MOTOR A STOP | COOLING WATER COOLER MOTOR B STOP
[7 empty] | TAG NO. | ESD2A-C-2101-C | ESD2-C-2101-C | PSOV-2201C | PSOV-2202C | PSOV-2203C | PSOV-2204C | PSOV-2205C | PSOV-2123C | XSS-2200C | XSP-2200C | XSS-2202C (Note1) | XSP-2202C | XSS-2203C | XSP-2203C | XSS-2221C | XSP-2221C | XSS-2222C | XSP-2222C | XSS-2223C | XSP-2223C | XSS-2201C | XSP-2201C | ESDL-2245C | XSS-2200C | XSP-2200C | XSS-2205C | XSS-2206C | XSP-2205C | XSP-2206C | XSS-2220C | XSS-2226C | XSP-2220C | XSP-2226C
TITLE | EQUIP. | TAG | Logic Diagram Document No. | P&ID Page No. | DESCRIPTION | INTERLOCK NO. | LOCATION | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | UCP 2101C | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | LCP 2101C | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC | MCC
SOUR GAS RECIPROCATING COMPRESSOR | C-2101 / C-2102 | TT-2203 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | CRANK CASE LUB OIL TEMPERATURE HIGH | I-30C | UCP 2101C | [13 empty] | SP
|  | TT-2203 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | CRANK CASE LUB OIL TEMPERATURE LOW | I-30C | UCP 2101C | [12 empty] | S
|  | PT-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL PRESSURE HIGH | I-20C | UCP 2101C | [11 empty] | SP
|  | PT-2204 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUB OIL PRESSURE LOW | I-20C | UCP 2101C | [10 empty] | S
|  | LT-2213 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER RESERVOIR LEVEL LOW LOW | I-22C | UCP 2101C | [15 empty] | SP |  | SP
|  | TT-2213 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER RESERVOIR TEMPERATURE LOW | I-26C | UCP 2101C | [18 empty] | S
|  | TT-2213 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER RESERVOIR TEMPERATURE HIGH | I-26C | UCP 2101C | [19 empty] | SP
|  | PT-2220 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER LINE PRESSURE LOW | I-25C | UCP 2101C | [14 empty] | S
|  | HSL-2242 C1 | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LOAD 0% SELECTOR SWITCH ON UCP | I-40C | UCP 2101C |  |  | C | C | C | C | O
|  | HSL-2242 C2 | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LOAD 25% SELECTOR SWITCH ON UCP | I-40C | UCP 2101C |  |  | O | C | C | O | C
|  | HSL-2242 C3 | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LOAD 50% SELECTOR SWITCH ON UCP (NOTE 1) | I-40C | UCP 2101C |  |  | C | E | C | O | O
|  | HSL-2242 C4 | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LOAD 75% SELECTOR SWITCH ON UCP | I-40C | UCP 2101C |  |  | O | O | O | O | C
|  | HSL-2242 C5 | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LOAD 100% SELECTOR SWITCH ON UCP | I-40C | UCP 2101C |  |  | O | O | O | O | O
|  | HST-2243 C | BK-GCS-HY-120-IN-DW-0006 | 9C of 10 | COMPRESSOR START P.B ON UCP |  | UCP 2101C | [8 empty] | S (Note2) |  | S | [5 empty] | S |  | S |  | S |  |  |  |  | S | S |  |  | S | S
|  | HSP-2243 C | BK-GCS-HY-120-IN-DW-0006 | 9C of 10 | COMPRESSOR STOP P.B ON UCP |  | UCP 2101C | T | T | C | C | C | C | O | C |  | SP | S | SP |  | SP |  | SP |  | SP |  | SP |  | SP | E |  | SP |  |  | SP | SP |  |  | SP | SP
|  | HST-2224 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | COMPRESSOR START P.B ON LCP | I-2224C | LCP 2101C | [8 empty] | S (Note3)
|  | HSP-2224 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | COMPRESSOR STOP P.B ON LCP | I-2224C | LCP 2101C | T | T | C | C | C | C | O | C |  | SP | S | SP |  | SP |  | SP |  | SP |  | SP |  | SP | E |  | SP |  |  | SP | SP |  |  | SP | SP
|  | HST-2202 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | AUXILIARY OIL PUMP MOTOR START P.B ON LCP | I-2202C | LCP 2101C | [10 empty] | S
|  | HSP-2202 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | AUXILIARY OIL PUMP MOTOR STOP P.B ON LCP | I-2202C | LCP 2101C | [11 empty] | SP
|  | HST-2203 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | OIL HEATER START P.B ON LCP | I-2203C | LCP 2101C | [12 empty] | S
|  | HSP-2203 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | OIL HEATER STOP P.B ON LCP | I-2203C | LCP 2101C | [13 empty] | SP
|  | HST-2221 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | AUXILIARY WATER PUMP MOTOR START P.B ON LCP | I-2221C | LCP 2101C | [14 empty] | S
|  | HSP-2221 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | AUXILIARY WATER PUMP MOTOR STOP P.B ON LCP | I-2221C | LCP 2101C | [15 empty] | SP
|  | HST-2222 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | MAIN WATER PUMP MOTOR START P.B ON LCP | I-2222C | LCP 2101C | [16 empty] | S
|  | HSP-2222 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | MAIN WATER PUMP MOTOR STOP P.B ON LCP | I-2222C | LCP 2101C | [17 empty] | SP
|  | HST-2223 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | WATER HEATER START P.B ON LCP | I-2223C | LCP 2101C | [18 empty] | S
|  | HSP-2223 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | WATER HEATER STOP P.B ON LCP | I-2223C | LCP 2101C | [19 empty] | SP
|  | HST-2201 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | LUBRICATOR MOTOR START P.B ON LCP | I-2201C | LCP 2101C | [20 empty] | S
|  | HSP-2201 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | LUBRICATOR MOTOR STOP P.B ON LCP | I-2201C | LCP 2101C | [21 empty] | SP
|  | HST-2200 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | LUBRICATOR HEATER ON P.B ON LCP | I-2200C | LCP 2101C | [23 empty] | S
|  | HSP-2200 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | LUBRICATOR HEATER OFF P.B ON LCP | I-2200C | LCP 2101C | [24 empty] | SP
|  | HST-2205 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | OIL COOLER MOTOR A START P.B ON LCP | I-2205C | LCP 2101C | [25 empty] | S
|  | HSP-2205 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | OIL COOLER MOTOR A STOP P.B ON LCP | I-2205C | LCP 2101C | [27 empty] | SP
|  | HST-2206 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | OIL COOLER MOTOR B START P.B ON LCP | I-2206C | LCP 2101C | [26 empty] | S
|  | HSP-2206 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | OIL COOLER MOTOR B STOP P.B ON LCP | I-2206C | LCP 2101C | [28 empty] | SP
|  | HST-2220 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | WATER COOLER MOTOR A START ON LCP | I-2220C | LCP 2101C | [29 empty] | S
|  | HSP-2220 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | WATER COOLER MOTOR A STOP ON LCP | I-2220C | LCP 2101C | [31 empty] | SP
|  | HST-2226 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | WATER COOLER MOTOR B START ON LCP | I-2226C | LCP 2101C | [30 empty] | S
|  | HSP-2226 C | BK-GCS-HY-120-IN-DW-0006 | 08C of 10 | WATER COOLER MOTOR B STOP ON LCP | I-2226C | LCP 2101C | [32 empty] | SP
|  | VS-2205 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUBE OIL AIR COOLER MOTOR A VIBRATION HIGH HIGH | I-62C | UCP 2101C | [27 empty] | SP
|  | VS-2206 C | BK-GCS-HY-120-IN-DW-0006 | 3C of 10 | LUBE OIL AIR COOLER MOTOR B VIBRATION HIGH HIGH | I-61C | UCP 2101C | [28 empty] | SP
|  | VS-2207 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER AIR COOLER MOTOR A VIBRATION HIGH HIGH | I-63C | UCP 2101C | [31 empty] | SP
|  | VS-2208 C | BK-GCS-HY-120-IN-DW-0006 | 5C of 10 | COOLING WATER AIR COOLER MOTOR B VIBRATION HIGH HIGH | I-64C | UCP 2101C | [32 empty] | SP
General Notes:
LEGEND: LCP: LOCAL CONTROL PANEL UCP: UNIT CONTROL PANEL MCC: MOTOR CONTROL CENTER |  |  |  | S: START SP: STOP T: TRIP O: OPEN C: CLOSE |  | NOTE 1: THE CRANK-END (PSOV-2201 C/ 2204 C) AND HEAD-END (PSOV-2202 C / 2203 C) SIDES WILL BE CHANGED ALTERNATELY AS MENTIONED IN CONTROL PHILOSOPHY ("BK-GCS-HY-120-PR-PH-0001"). NOTE 2: THE START PERMISSIVE REQUEST FROM UCP TO DCS, START PERMISSION OF UCP, AND START SEQUENCE (AUTOMATICALLY) SHALL BE CONSIDERED WHEN THE COMPRESSOR START IS FROM UCP. NOTE 3: BEFORE STARTING THE COMPRESSOR FROM LCP, PREHEATING AND PRELUBRICATION STEPS (DISCUSSED IN CONTROL PHILOSOPHY"BK-GCS-HY-120-PR-PH-0001") SHALL BE DONE BY OPERATOR VIA LCP.
شماره پیمان:
053 - 073 - 9184
BK
GCS
HY
120
IN
LI
0001
V04
پروژه
بسته کاری
صادر کننده
تسهیلات
رشته
نوع مدرک
سریال
نسخه
NISOC
نگهداشت و افزایش تولید میدان نفتی بینک
سطح الارض و ابنیه تحت الارض/بسته ایستگاه تقویت فشار گاز
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک
(قرارداد BK-HD-GCS-CO-0008_03)
شماره صفحه: 14 از 14
CAUSE AND EFFECT CHARTS LIST

## Messages (hidden)
Oval 931 | Sht 1
Oval 936 | Sht 1
Oval 1656 | Sht 1
Oval 87 | Sht 2
Oval 93 | Sht 2
Oval 94 | Sht 2
Oval 96 | Sht 2
Oval 502 | Sht 2
Oval 102 | Sht 2
Oval 89 | Sht 2
Oval 161 | Sht 4
Oval 525 | Sht 4
Oval 299 | Sht 4
Oval 209 | Sht 4
Rectangle 229 | Sht 4
Oval 241 | Sht 4
Oval 356 | Sht 5
Oval 349 | Sht 5
Oval 350 | Sht 5
Oval 581 | Sht 5
Oval 70 | Sht 11
Oval 71 | Sht 11
Oval 193 | Sht 12
Oval 192 | Sht 12
Oval 206 | Sht 12
Oval 196 | Sht 12
Oval 276 | Sht 13
Oval 277 | Sht 13
Oval 289 | Sht 13
Oval 321 | Sht 14
Oval 326 | Sht 14
Oval 546 | Sht 14
Oval 355 | Sht 14
Oval 358 | Sht 14
Oval 361 | Sht 14
Oval 369 | Sht 14
Oval 363 | Sht 14
Oval 371 | Sht 14
Oval 364 | Sht 14
Oval 372 | Sht 14