## COVER
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 15
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI | 0005 | V02
طرح نگهداشت و افزایش تولید 27 مخزن
I/O LIST نگهداشت و افزایش تولید میدان نفتی بینک
V02 |  | Jan.2025 |  | AFC |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  | S.Faramarzpour
V01 |  | Jan.2024 |  | IFR |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  | M.SADEGHIAN
V00 |  | MAY.2023 |  | IFR |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  | M.SADEGHIAN
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از15
9184 – 073 - 053 |  |  | BK | GCS |  | HY | 120 | IN | LI | 0005 |  | V02
REVISION RECORD SHEET
Page | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 | X | X | X | [5 empty] | 65
2 | X | X | X | [5 empty] | 66
3 | X | X | X | [5 empty] | 67
4 | X | X | X | [5 empty] | 68
5 | X | X | X | [5 empty] | 69
6 | X | X | X | [5 empty] | 70
7 | X | X | X | [5 empty] | 71
8 | X | X | X | [5 empty] | 72
9 | X | X | X | [5 empty] | 73
10 |  | X | X | [5 empty] | 74
11 |  | X | X | [5 empty] | 75
12 |  | X | X | [5 empty] | 76
13 |  | X | X | [5 empty] | 77
14 |  | X | X | [5 empty] | 78
15 |  | X | X | [5 empty] | 79
16 |  | X | [6 empty] | 80
17 |  | X | [6 empty] | 81
18 |  | X | [6 empty] | 82
19 |  | X | [6 empty] | 83
20 |  | X | [6 empty] | 84
21 |  | X | [6 empty] | 85
22 |  | X | [6 empty] | 86
23 |  | X | [6 empty] | 87
24 |  | X | [6 empty] | 88
25 |  | X | [6 empty] | 89
26 |  | X | [6 empty] | 90
27 |  | X | [6 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## LEGEND
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 15
9184 – 073 - 053 |  |  |  | BK | GCS | HY | 120 | IN | LI | 0005 | V02
ABBREVIATIONS
| Location: |  | (Geographical location of the instrument) | [6 empty] | Valve Action :
| FIELD | : | Local | [6 empty] | FC | : | Fail Close
| LCP | : | Local Panel | [6 empty] | FO | : | Fail Open
| SS | : | Electrical Substation | [6 empty] | FL | : | Fail Lock
| ITR | : | Instrument Technical Room | [6 empty] | FLC | : | Fail Lock Close
| CCR | : | Central Control Room | [6 empty] | FLO | : | Fail Lock Open
| MCC | : | Motor Control Center
| DCS | : | Distributed Control System
| ESD | : | Emergency Shutdown System | [6 empty] | W/D :
| UCP | : | Unit Control Panel | [6 empty] | D | : | Dry Contact
[10 empty] | W | : | Wet Contact
| I/O type | [8 empty] | Power Supply :
| AI | : | Analog Input | [6 empty] | AC110V
| AO | : | Analog Output | [6 empty] | DC24V
| DI | : | Digital Input
| DO | : | Digital Output
| DOR | : | Digital Output redundant
| AIR | : | Analog Input redundant
| AIRF | : | Analog Input redundant FAII SAFE
| AOR | : | Analog Output redundant
| DIR | : | Digital Input redundant
| DIRF | : | Digital Input redundant FAIL SAFE
| SAI | : | Software Analog Input
| SAO | : | Software Analog Output
| SDI | : | Software Digital Input
| SDO | : | Software Digital Output
| F |  | fail safe
System:
| ESD | : | Emergency Shut Down System
| UCP | : | Unit Control Panel
| DCS | : | Distributed Control System (PCS)
| FGS | : | Fire and Gas System
| MCC | : | Motor Control Center
Signal Type :
4-20mA
DC24V
| NC |  | Contact (Normal Close)
| NO |  | Contact (Normal Open)
| SOV |  | Digital Output Solenoid Valve
| SL |  | Serial Link
Refrence Doc:
BK-GCS-HY-120-PR-PI-0001 P&I DIAGRAM

## LIST-A
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | 4 از 15 |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V02
Item No. | LOOP NUMBER |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | POSV-2201A | POSV-2201A | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DORF | UCP-2101A | C-JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD POSV-2201A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
2 | POSV-2202A | POSV-2202A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DORF | UCP-2101A | C-JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD POSV-2202A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
3 | POSV-2203A | POSV-2203A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DORF | UCP-2101A | C-JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD POSV-2203A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
4 | POSV-2204A | POSV-2204A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DORF | UCP-2101A | C-JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD POSV-2204A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
5 | POSV-2205A | POSV-2205A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | DORF | UCP-2101A | C-JBU-S-2101A | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
| USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD POSV-2205A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
6 | FI-2121A | FT-2121A | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2121A |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
7 | TI-2122A | TT-2122A | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2122A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
8 | PDI-2122A | PDT-2122A | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-0.4 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2122A |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
9 | PI-2123A | PT-2123A | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 8" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2123A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
10 | TI-2123A | TT-2123A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2123A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
11 | PI-2124A | PT-2124A | A | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2124A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
12 | FI-2131A | FT-2131A | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2131A |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
13 | TI-2132A | TT-2132A | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2132A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
14 | PI-2132A | PT-2132A | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2132A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
15 | PDI-2132A | PDT-2132A | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-0.4 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2132A |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
16 | TI-2133A | TT-2133A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2133A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
17 | PI-2133A | PT-2133A | A | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | AI | JBU-A-2101 (Hirgan JB) | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-65 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2133A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
18 | PV-2123A | PV-2123A | A | CONTROLLER | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AOR | UCP-2101A | C-JBU-A-2101 (Hirgan JB) |  |  | 4-20mA | IS
|  | PVZ-2123A |  | Feed back |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | C-JBU-A-2101 (Hirgan JB) | UCP-2101A |  |  | 4-20mA | IS
|  | PVZI-2123A |  | Feed back |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS |  |  | 4-20mA | IS
19 |  | CZSO-2123A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DI | JBU-D-2103A (Hirgan JB) | UCP-2101A | 24VDC | W |  | NIS
20 |  | CZSC-2123A | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DI | JBU-D-2103A (Hirgan JB) | UCP-2101A | 24VDC | W |  | NIS
21 |  | POSV-2123A | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DORF | UCP-2101A | POSV-2123A | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
|  | USD-I-60A | A | Trip Relay Center in UCP Internal USD POSV-2123A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  |  | Trip Relay UCP A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
22 | TI-2203A | TT-2203A | A | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AIR | C-JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2203A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | DCS
23 | TI-2213A | TT-2213A | A | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | AIR | C-JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2213A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | DCS
24 | PI-2204A | PT-2204A | A | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | 2" |  |  | AIR | C-JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | DCS
25 | PI-2220A | PT-2220A | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | AIR | C-JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2220A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | DCS
26 | LI-2213A | LT-2213 A | A | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | AIR | C-JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-1350 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2213A |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | DCS
27 | TI-2191A | TT-2191A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | C-JBU-A-2101A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2191A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
28 | TI-2194A | TT-2194A | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | C-JBU-A-2101A | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2194A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
29 | TI-2231A | TT-2231A | A | TEMPERATURE TRANSMITTER | WATER HEATER | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | AI | C-JBU-A-2101A | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | Ti-2231A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | Serial link | UCP-2101A | DCS
30 | PI-2201A | PT-2201A | A | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A | 2" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2201A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 2A |  |  |  | Serial link | UCP-2101A | DCS
31 | PI-2210A | PT-2210A | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2210A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | Serial link | UCP-2101A | DCS
32 | PI-2211A | PT-2211A | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2211A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | Serial link | UCP-2101A | DCS
33 | PI-2212A | PT-2212A | A | PRESSURE TRANSMITTER | N2 TO Flare | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A | 1" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2212A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 4A |  |  |  | Serial link | UCP-2101A | DCS
34 | PI-2200A | PT-2200A | A | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2200A |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | DCS
35 | LI-2200A | LT-2200A | A | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-425 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2200A |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | DCS
36 | FI-2206A | FT-2206A | A | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 6A | 2" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.2 | m3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2206A |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 6A |  |  |  | Serial link | UCP-2101A | DCS
37 | TI-2204A | TT-2204A | A | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | 4" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2204A |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | DCS
38 | PDI-2204A | PDT-2204A | A | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | 1" |  |  | AI | C-JBU-A-2104A | UCP-2101A | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2204A |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | Serial link | UCP-2101A | DCS
39 | ZI-2200A | ZT-2200A | A | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | C-JBU-A-2102A | UCP-2101A | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2200A |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
40 | ZI-2201A | ZT-2201A | A | ROD DROP TRANSMITTER | Right Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | C-JBU-A-2102A | UCP-2101A | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2201A |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
41 | XI-2200A | XT-2200A | A | Key Phasor | Key Phasor | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AI | C-JBU-A-2102A | UCP-2101A | 24VDC | - | 4-20mA | IS |  | 1000 | Rpm |  |  |  |  | ZONE2, IIB, T4
|  | XI-2200A |  | Key Phasor |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
42 | TI-2214A | TT-2214A | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2214A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
43 | TI-2215A | TT-2215A | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2215A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
44 | TI-2216A | TT-2216A | A | TEMPERATURE TRANSMITTER | Com DE Bearing Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2216A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
45 | TI-2217A | TT-2217A | A | TEMPERATURE TRANSMITTER | Comp Packing RIGHT Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2217A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
46 | TI-2218A | TT-2218A | A | TEMPERATURE TRANSMITTER | Com NDE Bearing Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2218A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
47 | TI-2219A | TT-2219A | A | TEMPERATURE TRANSMITTER | Comp Packing LEFT Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2219A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
48 | TI-2220A | TT-2220A | A | TEMPERATURE TRANSMITTER | Com Mid Bearing Temp | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TI-2220A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
49 | TI-2221A | TT-2221A | A | TEMPERATURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TT-2221A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | Serial link | UCP-2101A | DCS
50 | VI-2200A | VT-2200A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | VI-2200A |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
51 | VI-2201A | VT-2201A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | VI-2201A |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
52 | VI-2202A | VT-2202A | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | _ | C-JBU-A-2103A | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC
|  | VI-2202A |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
53 | TI-2222A | TE-2222A | A | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC |  |  | 4-20mA
|  | TI-2222A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
54 | TI-2225A | TE-2225A | A | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC |  |  | 4-20mA
|  | TI-2225A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
55 | TI-2228A | TE-2228A | A | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | AIRF | Trip Relay UCP A | UCP-2101A PLC |  |  | 4-20mA
|  | TI-2228A |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | Serial link | UCP-2101A | DCS
56 | TI-2191A | TS-2191A | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | C-JBU-D-2101A | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 150 | °C
|  | TAHH-2191A |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | DIRF | Trip Relay UCP A | UCP-2101A PLC | 24VDC
|  | TAHH-2191A |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
57 | TI-2194A | TS-2194A | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | - | C-JBU-D-2101A | Trip Relay UCP A |  |  |  | NIS |  | 170 | °C
|  | TAHH-2194A |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A PLC
|  | TAHH-2194A |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
58 | PI-2133A | PS-2133A | A | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | 6" |  |  | - | C-JBU-D-2101A | Trip Relay UCP A |  |  |  | NIS |  | 57 | BARG
|  | PAHH-2133A |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A PLC
|  | PAHH-2133A |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 1A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
59 | PI-2204A | PS-2204A | A | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | - | C-JBU-D-2101A | Trip Relay UCP A |  |  |  | N'IS |  | 1.2 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PAHH-2204A |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A PLC
|  | PAHH-2204A |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
60 | PI-2220A | PS-2220A | A | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | 2" |  |  | - | C-JBU-D-2101A | Trip Relay UCP A |  |  |  | NIS |  | 2 | BARG
|  | PAHH-2220A |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIRF | Trip Relay UCP A | UCP-2101A PLC
|  | PAHH-2220A |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
61 | XSS-2200A | XSS-2200A | A | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
62 | XSP-2200A | XSP-2200A | A | STOP COMMAND HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
63 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
64 | XR-2200A | XR-2200A | A | RUNNING STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
65 | XF-2200A | XF-2200A | A | FAILURE STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
66 | XSS-2201A | XSS-2201A | A | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
67 | XSP-2201A | XSP-2201A | A | STOP COMMAND LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
68 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
69 | XR-2201A | XR-2201A | A | RUNNING STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
70 | XF-2201A | XF-2201A | A | FAILURE STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
71 | XSS-2202A | XSS-2202A | A | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XSP-2202A | XSP-2202A | A | STOP COMMAND AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
73 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
74 | XR-2202A | XR-2202A | A | RUNNING STATUSAUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XF-2202A | XF-2202A | A | FAILURE STATUS AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
75 | XSP-2203A | XSP-2203A | A | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE(H-2101-OH A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
76 | XSS-2203A | XSS-2203A | A | STOP COMMAND HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
77 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
78 | XR-2203A | XR-2203A | A | RUNNING STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
79 | XF-2203A | XF-2203A | A | FAILURE STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
80 | XSS-2205A | XSS-2205A | A | START COMMAND LUB OIL COOLER MOTOR A | LUB OIL COOLER (AE-2101-OC A1) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
81 | XSP-2205A | XSP-2205A | A | STOP COMMAND LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
82 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
83 | XR-2205A | XR-2205A | A | RUNNING STATUS LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
84 | XF-2205A | XF-2205A | A | FAILURE STATUS LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
85 | XSS-2206A | XSS-2206A | A | START COMMAND LUB OIL COOLER MOTOR B | LUB OIL COOLER (AE-2101-OC A2) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
86 | XSP-2206A | XSP-2206A | A | STOP COMMAND LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
87 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
88 | XR-2206A | XR-2206A | A | RUNNING STATUS LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
89 | XF-2206A | XF-2206A | A | FAILURE STATUS LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
90 | XSS-2220A | XSS-2220A | A | START COMMAND WATER CONSULE COOLER MOTOR A | WATER CONSULE COOLER (AE-2101-WC A1) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
91 | XSP-2220A | XSP-2220A | A | STOP COMMAND WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
92 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
93 | XR-2220A | XR-2220A | A | RUNNING STATUS WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
94 | XF-2220A | XF-2220A | A | FAILURE STATUS WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
95 | XSS-2220A | XSS-2220A | A | START COMMAND WATER CONSULE COOLER MOTOR B | WATER CONSULE COOLER (AE-2101-WC A2) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
96 | XSP-2220A | XSP-2220A | A | STOP COMMAND WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
97 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
98 | XR-2220A | XR-2220A | A | RUNNING STATUS WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
99 | XF-2220A | XF-2220A | A | FAILURE STATUS WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
100 | XSS-2221A | XSS-2221A | A | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
101 | XSP-2221A | XSP-2221A | A | STOP COMMAND AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
102 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
103 | XR-2221A | XR-2221A | A | RUNNING STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
104 | XF-2221A | XF-2221A | A | FAILURE STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
105 | XSS-2222A | XSS-2222A | A | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
106 | XSP-2222A | XSP-2222A | A | STOP COMMAND MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
107 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
108 | XR-2222A | XR-2222A | A | RUNNING STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
109 | XF-2222A | XF-2222A | A | FAILURE STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
110 | XSS-2223A | XSS-2223A | A | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (H-2101-WHA) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
111 | XSP-2223A | XSP-2223A | A | STOP COMMAND HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
112 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
113 | XR-2223A | XR-2223A | A | RUNNING STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
114 | XF-2223A | XF-2223A | A | FAILURE STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
115 | XSS-2224A | XSS-2224A | A | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR (M-2101-A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
116 | XSP-2224A | XSP-2224A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
117 | USD-I-60A | USD-I-60A | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
118 | XR-2224A | XR-2224A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
119 | XF-2224A | XF-2224A | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
120 | XSS-2225A | XSS-2225A | A | START COMMAND | MOTOR BEARING DEVICE MOTOR (M-2101-BM-A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
121 | XSP-2225A | XSP-2225A | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DOR | UCP-2101A | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
122 | XR-2225A | XR-2225A | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
123 | XF-2225A | XF-2225A | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | MCC | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
-
124 |  | HST-2203A | A | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
125 |  | HSP-2203A | A | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
126 |  | HSL-2203A | A | SELECTOR SWITCH | OIL HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
127 |  | HSR-2203A | A | SELECTOR SWITCH | OIL HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
128 |  | HST-2202A | A | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
129 |  | HSP-2202A | A | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
130 |  | HSL-2202A | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
131 |  | HSR-2202A | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
132 |  | HST-2200A | A | PUSH BUTTON | LUBRICATOR HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
133 |  | HSP-2200A | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
134 |  | HSL-2200A | A | SELECTOR SWITCH | LUBRICATOR HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
135 |  | HSR-2200A | A | SELECTOR SWITCH | LUBRICATOR HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
136 |  | HST-2201A | A | PUSH BUTTON | LUBRICATOR MOTOR ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
137 |  | HSP-2201A | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
138 |  | HSL-2201A | A | SELECTOR SWITCH | LUBRICATOR MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
139 |  | HSR-2201A | A | SELECTOR SWITCH | LUBRICATOR MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
140 |  | HST-2224A | A | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
141 |  | HSP-2224A | A | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
142 |  | HSL-2224A | A | SELECTOR SWITCH | MAIN MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
143 |  | HSR-2224A | A | SELECTOR SWITCH | MAIN MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
144 |  | HST-2205A | A | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
145 |  | HSP-2205A | A | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
146 |  | HSL-2205A | A | SELECTOR SWITCH | OIL COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
147 |  | HSR-2205A | A | SELECTOR SWITCH | OIL COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
148 |  | HST-2222A | A | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
149 |  | HSP-2222A | A | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
150 |  | HSL-2222A | A | SELECTOR SWITCH | MAIN WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
151 |  | HSR-2222A | A | SELECTOR SWITCH | MAIN WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
152 |  | HSL-2221A | A | SELECTOR SWITCH | AUX WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
153 |  | HST-2221A | A | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
154 |  | HSP-2221A | A | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
155 |  | HSL-2221A | A | SELECTOR SWITCH | AUX WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
156 |  | HSR-2221A | A | PUSH BUTTON | WATER HEATER ON PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
157 |  | HSL-2221A | A | PUSH BUTTON | WATER HEATER OFF PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
158 |  | HSL-2223A | A | SELECTOR SWITCH | WATER HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
159 |  | HSR-2223A | A | SELECTOR SWITCH | WATER HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
160 |  | HST-2223A | A | PUSH BUTTON | WATER COOLER MOTOR A START PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
161 |  | HSP-2223A | A | PUSH BUTTON | WATER COOLER MOTOR A STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
162 |  | HSL-2220A | A | SELECTOR SWITCH | WATER COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
163 |  | HSR--2220A | A | SELECTOR SWITCH | WATER COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
164 |  | HST--2225A | A | PUSH BUTTON | BARRING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
165 |  | HSP--2225A | A | PUSH BUTTON | BARRING MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
166 |  | HST-2206A | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
167 |  | HSP-2206A | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DI | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
168 |  | HSL-2206A | A | SELECTOR SWITCH | OIL COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
169 |  | HSR-2206A | A | SELECTOR SWITCH | OIL COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
170 |  | HST-2226A | A | PUSH BUTTON | WATER COOLER MOTOR B START PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
171 |  | HSP-2226A | A | PUSH BUTTON | WATER COOLER MOTOR B STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
172 |  | HSL-2226A | A | SELECTOR SWITCH | WATER COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
173 |  | HSR--2226A | A | SELECTOR SWITCH | WATER COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
174 |  | HSL-2241A | A | SELECTOR SWITCH | COMP LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
175 |  | HSR-2241A | A | SELECTOR SWITCH | COMP REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
176 |  | HSR-2243A | A | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
177 |  | HST-2241A | A | PUSH BUTTON | LAMP TEST PUSH BUTTON SWITCH | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DI | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
178 |  | ESDL-2245A | A | PUSH BUTTON | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DIRF | LCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
179 |  | HSL-2242A1 | A | SELECTOR SWITCH | LOAD 0% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DIR | UCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
180 |  | HSL-2242A2 | A | SELECTOR SWITCH | LOAD 25% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DIR | UCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
181 |  | HSL-2242A3 | A | SELECTOR SWITCH | LOAD 50% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DIR | UCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
182 |  | HSL-2242A4 | A | SELECTOR SWITCH | LOAD 75% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DIR | UCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
183 |  | HSL-2242A5 | A | SELECTOR SWITCH | LOAD 100% | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DIR | UCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
184 |  | XL-2203A | A | SIGNAL LAMP | OIL HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
185 |  | XL-2202A | A | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
186 |  | XL-2200A | A | SIGNAL LAMP | LUBRICATOR HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DO | UCP-2101A | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
187 |  | XL-2201A | A | SIGNAL LAMP | LUBRICATOR MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DO | UCP-2101A | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
188 |  | XL-2224A | A | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
189 |  | XL-2205A | A | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
190 |  | XL-2222A | A | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
191 |  | XL-2221A | A | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
192 |  | XL-2223A | A | SIGNAL LAMP | WATER HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
193 |  | XL-2220A | A | SIGNAL LAMP | WATER COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
194 |  | XL-2225A | A | SIGNAL LAMP | BARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 7A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
195 |  | XL-2206A | A | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 3A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
196 |  | XL-2226A | A | SIGNAL LAMP | WATER COOLER B RUNNING | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
197 |  | XSP-2245A | A | SIGNAL LAMP | COMP START PERMISSION | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
198 |  | XF-2245A | A | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
199 |  | ESDL-2245A | A | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A | - | - | - | DO | UCP-2101A | LCP-2101A | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
200 |  | ESDR2-C-2101-A | A | TRIP COMMAND | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIRF | ESD | UCP-2101A | 24VDC | W | 24VDC | NIS
201 |  | ESDR2-C-2101-A | A | TRIP COMMAND | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIRF | ESD | UCP-2101A | 24VDC | W | 24VDC | NIS
202 |  | ESD2A-C-2101-A | A | TRIP FEEDBACK | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DORF | UCP-2101A | ESD | 24VDC | D | 24VDC | NIS
203 |  | ESD2-C-2101-A | A | TRIP FEEDBACK | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DORF | UCP-2101A | ESD | 24VDC | D | 24VDC | NIS
204 |  | PI-2121A | A | SPILL BACK | SPILL BACK | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | AIR | DCS | UCP-2101A | 24VDC | - | 4-20mA | NIS |  | BY CLIENT | BARG
205 |  | XS-2100A | A | Time Syc |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DI | DCS | UCP-2101A | 24VDC | W | 24VDC | NIS
206 |  | XSS-2123A | A | Permission to star |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DIR | DCS | UCP-2101A | 24VDC | W | 24VDC | NIS
207 |  | XSS-2124A | A | Ready to Start |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DO | UCP-2101A | DCS | 24VDC | D | 24VDC | NIS
208 |  | XR-2124A | A | Running Status |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1A |  |  |  | DO | UCP-2101A | DCS | 24VDC | D | 24VDC | NIS
209 |  | HSS-2126A | A | Request start Permission |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-HY-120-PR-PI-0001-SHEET 9A |  |  |  | DO | UCP-2101A | FCS | 24VDC | D | 24VDC | NIS
210 |  | HST-2243A | A | COMPRESSOR START P.B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 9A |  |  |  | DI | UCP-2101A | UCP-2101A | 24VDC | D | 24VDC | NIS
211 |  | HSP-2243A | A | COMPRESSOR STOP P.B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 9A |  |  |  | DI | UCP-2101A | UCP-2101A | 24VDC | D | 24VDC | NIS
212 |  | HSR-2243A | A | COMPRESSOR RESET P.B |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 9A |  |  |  | DI | UCP-2101A | UCP-2101A | 24VDC | D | 24VDC | NIS
213 |  | ESD-2231A | A | EMERGENCY SHUT DOWN P.B | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 8A |  |  |  | DIRF | UCP-2101A | UCP-2101A | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
214 | VI-2205A | VS-2205A | A | VIBRATION SWITCH | LUB OIL COOLER (AE-2101-OC A1) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIR | C-JBU-D-2102A | UCP-2101A |  |  |  | NIS
|  | VAHH-2205A |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
215 | VI-2206A | VS-2206A | A | VIBRATION SWITCH | LUB OIL COOLER (AE-2101-OC A2) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIR | C-JBU-D-2102A | UCP-2101A |  |  |  | NIS
|  | VAHH-2206A |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
216 | VI-2207A | VS-2207A | A | VIBRATION SWITCH | WATER CONSULE COOLER (AE-2101-WC A1) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIR | C-JBU-D-2102A | UCP-2101A |  |  |  | NIS
|  | VAHH-2207A |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
217 | VI-2208A | VS-2208A | A | VIBRATION SWITCH | WATER CONSULE COOLER (AE-2101-WC A2) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIR | C-JBU-D-2102A | UCP-2101A |  |  |  | NIS
|  | VAHH-2208A |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A | - | - | - | Serial link | UCP-2101A | DCS | 24VDC
218 | XZSO-2225A | XZSO-2225A | A | BEARING DEVICE LIMIT SWITCH FEEDBACK | BEARING DEVICE (C-2101-BD A) | PACKAGE COMPRESSOR C-2101A | BK-GCS-HY-120-PR-PI-0001-SHEET 5A |  |  |  | DIR | C-JBU-D-2102A | UCP-2101A |  |  |  | NIS
I/O Summery
|  |  | Num | Signal type | Quantity | 20% Spare | Total
|  |  | 1 | AI | 28 | 5.6 | 34
|  |  | 2 | AIR | 6 | 1.2 | 8
|  |  | 3 | AIRF | 14 | 2.8 | 17
|  |  | 4 | AOR | 1 | 1 | 2
|  |  | 5 | DI | 86 | 17.2 | 104
|  |  | 6 | DIR | 11 | 2.2 | 13
|  |  | 7 | DIRF | 9 | 1.8 | 11
|  |  | 8 | DO | 19 | 3.8 | 23
|  |  | 9 | DOR | 26 | 5.2 | 32
|  |  | 10 | DORF | 8 | 1.6 | 10
Note on B177: Forouzandeh Fatemeh: ALARM L,H چک شود
Note on C177: Forouzandeh Fatemeh: ALARM L,H چک شود
03

## LIST-B
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | 4 از 15 |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V02
Item No. | LOOP NUMBER |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | POSV-2201B | POSV-2201B | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DORF | UCP-2101B | C-JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD POSV-2201B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
2 | POSV-2202B | POSV-2202B | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DORF | UCP-2101B | C-JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD POSV-2202B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
3 | POSV-2203B | POSV-2203B | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DORF | UCP-2101B | C-JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD POSV-2203B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
4 | POSV-2204B | POSV-2204B | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DORF | UCP-2101B | C-JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD POSV-2204B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
5 | POSV-2205B | POSV-2205B | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | DORF | UCP-2101B | C-JBU-S-2101B | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
| USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD POSV-2205B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
6 | FI-2121B | FT-2121B | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2121B |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
7 | TI-2122B | TT-2122B | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2122B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
8 | PDI-2122B | PDT-2122B | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-0.4 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2122B |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
9 | PI-2123B | PT-2123B | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 8" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2123B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
10 | TI-2123B | TT-2123B | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2123B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
11 | PI-2124B | PT-2124B | A | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2124B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
12 | FI-2131B | FT-2131B | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2131B |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
13 | TI-2132B | TT-2132B | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2132B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
14 | PI-2132B | PT-2132B | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2132B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
15 | PDI-2132B | PDT-2132B | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-0.4 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2132B |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
16 | TI-2133B | TT-2133B | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2133B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
17 | PI-2133B | PT-2133B | A | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-65 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2133B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
18 | PV-2123B | PV-2123B | A | CONTROLLER | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AOR | UCP-2101B | JBU-A-2102 (Hirgan JB) |  |  | 4-20mA | IS
|  | PVZ-2123B |  | Feed back |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | JBU-A-2102 (Hirgan JB) | UCP-2101B |  |  | 4-20mA | IS
|  | PVZI-2123B |  | Feed back |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS |  |  | 4-20mA | IS
19 |  | CZSO-2123B | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | JBU-D-2103B (Hirgan JB) | UCP-2101B | 24VDC | W |  | NIS
20 |  | CZSC-2123B | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DI | JBU-D-2103B (Hirgan JB) | UCP-2101B | 24VDC | W |  | NIS
21 |  | POSV-2123B | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DORF | UCP-2101B | POSV-2123B | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
|  | USD-I-60B | A | Trip Relay Center in UCP Internal USD POSV-2123B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  |  | Trip Relay UCP A | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
22 | TI-2203B | TT-2203B | A | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AIR | C-JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2203B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | DCS
23 | TI-2213B | TT-2213B | A | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | AIR | C-JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2213B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | DCS
24 | PI-2204B | PT-2204B | A | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 2" |  |  | AIR | C-JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | DCS
25 | PI-2220B | PT-2220B | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | AIR | C-JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2220B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | DCS
26 | LI-2213B | LT-2213 A | A | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | AIR | C-JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-1350 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2213B |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | DCS
27 | TI-2191B | TT-2191B | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | C-JBU-A-2101B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2191B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
28 | TI-2194B | TT-2194B | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | C-JBU-A-2101B | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2194B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
29 | TI-2231B | TT-2231B | A | TEMPERATURE TRANSMITTER | WATER HEATER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | AI | C-JBU-A-2101B | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | Ti-2231B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | Serial link | UCP-2101B | DCS
30 | PI-2201B | PT-2201B | A | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B | 2" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2201B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 2B |  |  |  | Serial link | UCP-2101B | DCS
31 | PI-2210B | PT-2210B | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2210B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | Serial link | UCP-2101B | DCS
32 | PI-2211B | PT-2211B | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2211B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | Serial link | UCP-2101B | DCS
33 | PI-2212B | PT-2212B | A | PRESSURE TRANSMITTER | N2 TO Flare | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B | 1" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2212B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 4B |  |  |  | Serial link | UCP-2101B | DCS
34 | PI-2200B | PT-2200B | A | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2200B |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | DCS
35 | LI-2200B | LT-2200B | A | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-425 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2200B |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | DCS
36 | FI-2206B | FT-2206B | A | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 6B | 2" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.2 | m3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2206B |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 6B |  |  |  | Serial link | UCP-2101B | DCS
37 | TI-2204B | TT-2204B | A | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 4" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2204B |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | DCS
38 | PDI-2204B | PDT-2204B | A | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | 1" |  |  | AI | C-JBU-A-2104B | UCP-2101B | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2204B |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | Serial link | UCP-2101B | DCS
39 | ZI-2200B | ZT-2200B | A | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | C-JBU-A-2102B | UCP-2101B | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2200B |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
40 | ZI-2201B | ZT-2201B | A | ROD DROP TRANSMITTER | Right Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | C-JBU-A-2102B | UCP-2101B | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2201B |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
41 | XI-2200B | XT-2200B | A | Key Phasor | Key Phasor | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AI | C-JBU-A-2102B | UCP-2101B | 24VDC | - | 4-20mA | IS |  | 1000 | Rpm |  |  |  |  | ZONE2, IIB, T4
|  | XI-2200B |  | Key Phasor |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
42 | TI-2214B | TT-2214B | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2214B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
43 | TI-2215B | TT-2215B | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2215B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
44 | TI-2216B | TT-2216B | A | TEMPERATURE TRANSMITTER | Com DE Bearing Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2216B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
45 | TI-2217B | TT-2217B | A | TEMPERATURE TRANSMITTER | Comp Packing RIGHT Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2217B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
46 | TI-2218B | TT-2218B | A | TEMPERATURE TRANSMITTER | Com NDE Bearing Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2218B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
47 | TI-2219B | TT-2219B | A | TEMPERATURE TRANSMITTER | Comp Packing LEFT Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2219B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
48 | TI-2220B | TT-2220B | A | TEMPERATURE TRANSMITTER | Com Mid Bearing Temp | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TI-2220B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
49 | TI-2221B | TT-2221B | A | TEMPERATURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TT-2221B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | Serial link | UCP-2101B | DCS
50 | VI-2200B | VT-2200B | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | VI-2200B |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
51 | VI-2201B | VT-2201B | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | VI-2201B |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
52 | VI-2202B | VT-2202B | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | _ | C-JBU-A-2103B | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC
|  | VI-2202B |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
53 | TI-2222B | TE-2222B | A | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC |  |  | 4-20mA
|  | TI-2222B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
54 | TI-2225B | TE-2225B | A | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC |  |  | 4-20mA
|  | TI-2225B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
55 | TI-2228B | TE-2228B | A | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | AIRF | Trip Relay UCP A | UCP-2101B PLC |  |  | 4-20mA
|  | TI-2228B |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | Serial link | UCP-2101B | DCS
56 | TI-2191B | TS-2191B | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | C-JBU-D-2101B | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 150 | °C
|  | TAHH-2191B |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | DIRF | Trip Relay UCP A | UCP-2101B PLC | 24VDC
|  | TAHH-2191B |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
57 | TI-2194B | TS-2194B | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | - | C-JBU-D-2101B | Trip Relay UCP A |  |  |  | NIS |  | 170 | °C
|  | TAHH-2194B |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B PLC
|  | TAHH-2194B |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
58 | PI-2133B | PS-2133B | A | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | 6" |  |  | - | C-JBU-D-2101B | Trip Relay UCP A |  |  |  | NIS |  | 57 | BARG
|  | PAHH-2133B |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B PLC
|  | PAHH-2133B |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 1B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
59 | PI-2204B | PS-2204B | A | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | - | C-JBU-D-2101B | Trip Relay UCP A |  |  |  | N'IS |  | 1.2 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PAHH-2204B |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B PLC
|  | PAHH-2204B |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
60 | PI-2220B | PS-2220B | A | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | 2" |  |  | - | C-JBU-D-2101B | Trip Relay UCP A |  |  |  | NIS |  | 2 | BARG
|  | PAHH-2220B |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIRF | Trip Relay UCP A | UCP-2101B PLC
|  | PAHH-2220B |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
61 | XSS-2200B | XSS-2200B | A | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
62 | XSP-2200B | XSP-2200B | A | STOP COMMAND HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
63 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
64 | XR-2200B | XR-2200B | A | RUNNING STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
65 | XF-2200B | XF-2200B | A | FAILURE STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
66 | XSS-2201B | XSS-2201B | A | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
67 | XSP-2201B | XSP-2201B | A | STOP COMMAND LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
68 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
69 | XR-2201B | XR-2201B | A | RUNNING STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
70 | XF-2201B | XF-2201B | A | FAILURE STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
71 | XSS-2202B | XSS-2202B | A | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XSP-2202B | XSP-2202B | A | STOP COMMAND AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
73 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
74 | XR-2202B | XR-2202B | A | RUNNING STATUSAUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XF-2202B | XF-2202B | A | FAILURE STATUS AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
75 | XSP-2203B | XSP-2203B | A | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE(H-2101-OH B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
76 | XSS-2203B | XSS-2203B | A | STOP COMMAND HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
77 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
78 | XR-2203B | XR-2203B | A | RUNNING STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
79 | XF-2203B | XF-2203B | A | FAILURE STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
80 | XSS-2205B | XSS-2205B | A | START COMMAND LUB OIL COOLER MOTOR A | LUB OIL COOLER (AE-2101-OC B1) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
81 | XSP-2205B | XSP-2205B | A | STOP COMMAND LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
82 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
83 | XR-2205B | XR-2205B | A | RUNNING STATUS LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
84 | XF-2205B | XF-2205B | A | FAILURE STATUS LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
85 | XSS-2206B | XSS-2206B | A | START COMMAND LUB OIL COOLER MOTOR B | LUB OIL COOLER (AE-2101-OC B2) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
86 | XSP-2206B | XSP-2206B | A | STOP COMMAND LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
87 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
88 | XR-2206B | XR-2206B | A | RUNNING STATUS LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
89 | XF-2206B | XF-2206B | A | FAILURE STATUS LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
90 | XSS-2220B | XSS-2220B | A | START COMMAND WATER CONSULE COOLER MOTOR A | WATER CONSULE COOLER (AE-2101-WC B1) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
91 | XSP-2220B | XSP-2220B | A | STOP COMMAND WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
92 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
93 | XR-2220B | XR-2220B | A | RUNNING STATUS WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
94 | XF-2220B | XF-2220B | A | FAILURE STATUS WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
95 | XSS-2220B | XSS-2220B | A | START COMMAND WATER CONSULE COOLER MOTOR B | WATER CONSULE COOLER (AE-2101-WC B2) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
96 | XSP-2220B | XSP-2220B | A | STOP COMMAND WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
97 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
98 | XR-2220B | XR-2220B | A | RUNNING STATUS WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
99 | XF-2220B | XF-2220B | A | FAILURE STATUS WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
100 | XSS-2221B | XSS-2221B | A | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
101 | XSP-2221B | XSP-2221B | A | STOP COMMAND AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
102 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
103 | XR-2221B | XR-2221B | A | RUNNING STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
104 | XF-2221B | XF-2221B | A | FAILURE STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
105 | XSS-2222B | XSS-2222B | A | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
106 | XSP-2222B | XSP-2222B | A | STOP COMMAND MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
107 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
108 | XR-2222B | XR-2222B | A | RUNNING STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
109 | XF-2222B | XF-2222B | A | FAILURE STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
110 | XSS-2223B | XSS-2223B | A | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (H-2101-WHB) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
111 | XSP-2223B | XSP-2223B | A | STOP COMMAND HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
112 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
113 | XR-2223B | XR-2223B | A | RUNNING STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
114 | XF-2223B | XF-2223B | A | FAILURE STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
115 | XSS-2224B | XSS-2224B | A | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR (M-2101-B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
116 | XSP-2224B | XSP-2224B | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
117 | USD-I-60B | USD-I-60B | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
118 | XR-2224B | XR-2224B | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
119 | XF-2224B | XF-2224B | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
120 | XSS-2225B | XSS-2225B | A | START COMMAND | MOTOR BEARING DEVICE MOTOR (M-2101-BM-B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
121 | XSP-2225B | XSP-2225B | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DOR | UCP-2101B | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
122 | XR-2225B | XR-2225B | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
123 | XF-2225B | XF-2225B | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | MCC | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
-
124 |  | HST-2203B | A | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
125 |  | HSP-2203B | A | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
126 |  | HSL-2203B | A | SELECTOR SWITCH | OIL HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
127 |  | HSR-2203B | A | SELECTOR SWITCH | OIL HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
128 |  | HST-2202B | A | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
129 |  | HSP-2202B | A | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
130 |  | HSL-2202B | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
131 |  | HSR-2202B | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
132 |  | HST-2200B | A | PUSH BUTTON | LUBRICATOR HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
133 |  | HSP-2200B | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
134 |  | HSL-2200B | A | SELECTOR SWITCH | LUBRICATOR HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
135 |  | HSR-2200B | A | SELECTOR SWITCH | LUBRICATOR HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
136 |  | HST-2201B | A | PUSH BUTTON | LUBRICATOR MOTOR ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
137 |  | HSP-2201B | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
138 |  | HSL-2201B | A | SELECTOR SWITCH | LUBRICATOR MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
139 |  | HSR-2201B | A | SELECTOR SWITCH | LUBRICATOR MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
140 |  | HST-2224B | A | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
141 |  | HSP-2224B | A | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
142 |  | HSL-2224B | A | SELECTOR SWITCH | MAIN MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
143 |  | HSR-2224B | A | SELECTOR SWITCH | MAIN MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
144 |  | HST-2205B | A | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
145 |  | HSP-2205B | A | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
146 |  | HSL-2205B | A | SELECTOR SWITCH | OIL COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
147 |  | HSR-2205B | A | SELECTOR SWITCH | OIL COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
148 |  | HST-2222B | A | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
149 |  | HSP-2222B | A | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
150 |  | HSL-2222B | A | SELECTOR SWITCH | MAIN WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
151 |  | HSR-2222B | A | SELECTOR SWITCH | MAIN WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
152 |  | HSL-2221B | A | SELECTOR SWITCH | AUX WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
153 |  | HST-2221B | A | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
154 |  | HSP-2221B | A | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
155 |  | HSL-2221B | A | SELECTOR SWITCH | AUX WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
156 |  | HSR-2221B | A | PUSH BUTTON | WATER HEATER ON PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
157 |  | HSL-2221B | A | PUSH BUTTON | WATER HEATER OFF PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
158 |  | HSL-2223B | A | SELECTOR SWITCH | WATER HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
159 |  | HSR-2223B | A | SELECTOR SWITCH | WATER HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
160 |  | HST-2223B | A | PUSH BUTTON | WATER COOLER MOTOR A START PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
161 |  | HSP-2223B | A | PUSH BUTTON | WATER COOLER MOTOR A STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
162 |  | HSL-2220B | A | SELECTOR SWITCH | WATER COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
163 |  | HSR--2220B | A | SELECTOR SWITCH | WATER COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
164 |  | HST--2225B | A | PUSH BUTTON | BARRING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
165 |  | HSP--2225B | A | PUSH BUTTON | BARRING MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
166 |  | HST-2206B | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
167 |  | HSP-2206B | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DI | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
168 |  | HSL-2206B | A | SELECTOR SWITCH | OIL COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
169 |  | HSR-2206B | A | SELECTOR SWITCH | OIL COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
170 |  | HST-2226B | A | PUSH BUTTON | WATER COOLER MOTOR B START PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
171 |  | HSP-2226B | A | PUSH BUTTON | WATER COOLER MOTOR B STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
172 |  | HSL-2226B | A | SELECTOR SWITCH | WATER COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
173 |  | HSR--2226B | A | SELECTOR SWITCH | WATER COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
174 |  | HSL-2241B | A | SELECTOR SWITCH | COMP LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
175 |  | HSR-2241B | A | SELECTOR SWITCH | COMP REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
176 |  | HSR-2243B | A | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
177 |  | HST-2241B | A | PUSH BUTTON | LAMP TEST PUSH BUTTON SWITCH | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DI | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
178 |  | ESDL-2245B | A | PUSH BUTTON | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DIRF | LCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
179 |  | HSL-2242B1 | A | SELECTOR SWITCH | LOAD 0% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DIR | UCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
180 |  | HSL-2242B2 | A | SELECTOR SWITCH | LOAD 25% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DIR | UCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
181 |  | HSL-2242B3 | A | SELECTOR SWITCH | LOAD 50% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DIR | UCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
182 |  | HSL-2242B4 | A | SELECTOR SWITCH | LOAD 75% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DIR | UCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
183 |  | HSL-2242B5 | A | SELECTOR SWITCH | LOAD 100% | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DIR | UCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
184 |  | XL-2203B | A | SIGNAL LAMP | OIL HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
185 |  | XL-2202B | A | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
186 |  | XL-2200B | A | SIGNAL LAMP | LUBRICATOR HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DO | UCP-2101B | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
187 |  | XL-2201B | A | SIGNAL LAMP | LUBRICATOR MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DO | UCP-2101B | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
188 |  | XL-2224B | A | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
189 |  | XL-2205B | A | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
190 |  | XL-2222B | A | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
191 |  | XL-2221B | A | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
192 |  | XL-2223B | A | SIGNAL LAMP | WATER HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
193 |  | XL-2220B | A | SIGNAL LAMP | WATER COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
194 |  | XL-2225B | A | SIGNAL LAMP | BARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 7B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
195 |  | XL-2206B | A | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 3B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
196 |  | XL-2226B | A | SIGNAL LAMP | WATER COOLER B RUNNING | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
197 |  | XSP-2245B | A | SIGNAL LAMP | COMP START PERMISSION | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
198 |  | XF-2245B | A | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
199 |  | ESDL-2245B | A | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B | - | - | - | DO | UCP-2101B | LCP-2101B | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
200 |  | ESDR2-C-2101-A | A | TRIP COMMAND | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIRF | ESD | UCP-2101B | 24VDC | W | 24VDC | NIS
201 |  | ESDR2-C-2101-A | A | TRIP COMMAND | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIRF | ESD | UCP-2101B | 24VDC | W | 24VDC | NIS
202 |  | ESD2B-C-2101-A | A | TRIP FEEDBACK | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DORF | UCP-2101B | ESD | 24VDC | D | 24VDC | NIS
203 |  | ESD2-C-2101-A | A | TRIP FEEDBACK | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DORF | UCP-2101B | ESD | 24VDC | D | 24VDC | NIS
204 |  | PI-2121B | A | SPILL BACK | SPILL BACK | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | AIR | DCS | UCP-2101B | 24VDC | - | 4-20mA | NIS |  | BY CLIENT | BARG
205 |  | XS-2100B | A | Time Syc |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DI | DCS | UCP-2101B | 24VDC | W | 24VDC | NIS
206 |  | XSS-2123B | A | Permission to star |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DIR | DCS | UCP-2101B | 24VDC | W | 24VDC | NIS
207 |  | XSS-2124B | A | Ready to Start |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DO | UCP-2101B | DCS | 24VDC | D | 24VDC | NIS
208 |  | XR-2124B | A | Running Status |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1B |  |  |  | DO | UCP-2101B | DCS | 24VDC | D | 24VDC | NIS
209 |  | HSS-2126B | A | Request start Permission |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-HY-120-PR-PI-0001-SHEET 9B |  |  |  | DO | UCP-2101B | FCS | 24VDC | D | 24VDC | NIS
210 |  | HST-2243B | A | COMPRESSOR START P.B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 9B |  |  |  | DI | UCP-2101B | UCP-2101B | 24VDC | D | 24VDC | NIS
211 |  | HSP-2243B | A | COMPRESSOR STOP P.B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 9B |  |  |  | DI | UCP-2101B | UCP-2101B | 24VDC | D | 24VDC | NIS
212 |  | HSR-2243B | A | COMPRESSOR RESET P.B |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 9B |  |  |  | DI | UCP-2101B | UCP-2101B | 24VDC | D | 24VDC | NIS
213 |  | ESD-2231B | A | EMERGENCY SHUT DOWN P.B | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 8B |  |  |  | DIRF | UCP-2101B | UCP-2101B | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
214 | VI-2205B | VS-2205B | A | VIBRATION SWITCH | LUB OIL COOLER (AE-2101-OC B1) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIR | C-JBU-D-2102B | UCP-2101B |  |  |  | NIS
|  | VAHH-2205B |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
215 | VI-2206B | VS-2206B | A | VIBRATION SWITCH | LUB OIL COOLER (AE-2101-OC B2) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIR | C-JBU-D-2102B | UCP-2101B |  |  |  | NIS
|  | VAHH-2206B |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
216 | VI-2207B | VS-2207B | A | VIBRATION SWITCH | WATER CONSULE COOLER (AE-2101-WC B1) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIR | C-JBU-D-2102B | UCP-2101B |  |  |  | NIS
|  | VAHH-2207B |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
217 | VI-2208B | VS-2208B | A | VIBRATION SWITCH | WATER CONSULE COOLER (AE-2101-WC B2) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIR | C-JBU-D-2102B | UCP-2101B |  |  |  | NIS
|  | VAHH-2208B |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B | - | - | - | Serial link | UCP-2101B | DCS | 24VDC
218 | XZSO-2225B | XZSO-2225B | A | BEARING DEVICE LIMIT SWITCH FEEDBACK | BEARING DEVICE (C-2101-BD B) | PACKAGE COMPRESSOR C-2101B | BK-GCS-HY-120-PR-PI-0001-SHEET 5B |  |  |  | DIR | C-JBU-D-2102B | UCP-2101B |  |  |  | NIS
I/O Summery
|  |  | Num | Signal type | Quantity | 20% Spare | Total
|  |  | 1 | AI | 28 | 5.6 | 34
|  |  | 2 | AIR | 6 | 1.2 | 8
|  |  | 3 | AIRF | 14 | 2.8 | 17
|  |  | 4 | AOR | 1 | 1 | 2
|  |  | 5 | DI | 86 | 17.2 | 104
|  |  | 6 | DIR | 11 | 2.2 | 13
|  |  | 7 | DIRF | 9 | 1.8 | 11
|  |  | 8 | DO | 19 | 3.8 | 23
|  |  | 9 | DOR | 26 | 5.2 | 32
|  |  | 10 | DORF | 8 | 1.6 | 10
Note on B177: Forouzandeh Fatemeh: ALARM L,H چک شود
Note on C177: Forouzandeh Fatemeh: ALARM L,H چک شود
03

## LIST-C
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
I/O LIST
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه |  | 4 از 15 |  |  |  |  | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | HY |  |  | 120 |  | IN | LI |  | 0005 | V02
Item No. | LOOP NUMBER |  |  | Description | Service 1 | Service 2 | P&ID No. | line Size | Connection |  | I/O Type |  | Location, Signal (To) | Power Supply | W/D | Signal Type | IS/NIS | Valve Action | Range/ Alarm Set point | Eng. Units | Engineering Documents |  |  |  | Hazardous Area | Manufacturer | Model Number | Remark
|  | Tag Number | Unit Number | [5 empty] | Size | Rating |  | Location, Signal ( From) | [8 empty] | Loop Diagram No. | Inst. Location Layout | Hook-Up Drawing | Data Sheet
1 | POSV-2201C | POSV-2201C | A | SOLENOID VALVE | INST. AIR SUPPLY | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DORF | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD POSV-2201C |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
2 | POSV-2202C | POSV-2202C | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DORF | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD POSV-2202C |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
3 | POSV-2203C | POSV-2203C | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DORF | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD POSV-2203C |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
4 | POSV-2204C | POSV-2204C | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DORF | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO CLOSE | [6 empty] | ZONE2, IIB, T4
| USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD POSV-2204C |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
5 | POSV-2205C | POSV-2205C | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | DORF | UCP-2101C | JBU-S-2101C | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
| USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD POSV-2205C |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
6 | FI-2121C | FT-2121C | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2121C |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
7 | TI-2122C | TT-2122C | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2122C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
8 | PDI-2122C | PDT-2122C | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-0.4 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2122C |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
9 | PI-2123C | PT-2123C | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 1S STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 8" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2123C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
10 | TI-2123C | TT-2123C | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2123C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
11 | PI-2124C | PT-2124C | A | PRESSURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2124C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
12 | FI-2131C | FT-2131C | A | FLOW TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.1 | Nm3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2131C |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
13 | TI-2132C | TT-2132C | A | TEMPERATURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2132C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
14 | PI-2132C | PT-2132C | A | PRESSURE TRANSMITTER | ON SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-25 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2132C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
15 | PDI-2132C | PDT-2132C | A | DIFF. PRESSURE TRANSMITTER | STRAINER FILTER SUCTION SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-0.4 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2132C |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
16 | TI-2133C | TT-2133C | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2133C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
17 | PI-2133C | PT-2133C | A | PRESSURE TRANSMITTER | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | AI | JBU-A-2105C (Hirgan JC) | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-65 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2133C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
18 | PV-2123C | PV-2123C | A | CONTROLLER | SPILL BACK VALVE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AOR | UCP-2101C | JBU-A-2103 (Hirgan JB) |  |  | 4-20mA | IS
|  | PVZ-2123C |  | Feed back |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2103 (Hirgan JB) | UCP-2101C |  |  | 4-20mA | IS
|  | PVZI-2123C |  | Feed back |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS |  |  | 4-20mA | IS
19 |  | CZSO-2123C | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DI | JBU-D-2103C (Hirgan JC) | UCP-2101C | 24VDC | W |  | NIS
20 |  | CZSC-2123C | A | LIMIT SWITCH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DI | JBU-D-2103C (Hirgan JC) | UCP-2101C | 24VDC | W |  | NIS
21 |  | POSV-2123C | A | SOLENOID VALVE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DORF | UCP-2101C | POSV-2123C | 24VDC | W | 24VDC | NIS | FAIL TO OPEN | [6 empty] | ZONE2, IIB, T4
|  | USD-I-60C | A | Trip Relay Center in UCP Internal USD POSV-2123C |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  |  | Trip Relay UCP A | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
22 | TI-2203C | TT-2203C | A | TEMPERATURE TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AIR | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2203C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | DCS
23 | TI-2213C | TT-2213C | A | TEMPERATURE TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | AIR | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2213C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | DCS
24 | PI-2204C | PT-2204C | A | PRESSURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 2" |  |  | AIR | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2204C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | DCS
25 | PI-2220C | PT-2220C | A | PRESSURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | AIR | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2220C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | DCS
26 | LI-2213C | LT-2213 A | A | LEVEL TRANSMITTER | WATER RESERVOIR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | AIR | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-1350 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2213C |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | DCS
27 | TI-2191C | TT-2191C | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2101C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2191C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
28 | TI-2194C | TT-2194C | A | TEMPERATURE TRANSMITTER | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2101C | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2194C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
29 | TI-2231C | TT-2231C | A | TEMPERATURE TRANSMITTER | WATER HEATER | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | AI | JBU-A-2101C | CCR | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
|  | Ti-2231C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | Serial link | UCP-2101C | DCS
30 | PI-2201C | PT-2201C | A | PRESSURE TRANSMITTER | ON INSTRUMENT LINE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C | 2" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-16 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2201C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 2C |  |  |  | Serial link | UCP-2101C | DCS
31 | PI-2210C | PT-2210C | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2210C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | Serial link | UCP-2101C | DCS
32 | PI-2211C | PT-2211C | A | PRESSURE TRANSMITTER | N2 TO CYLINDER PACKING INLET | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2211C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | Serial link | UCP-2101C | DCS
33 | PI-2212C | PT-2212C | A | PRESSURE TRANSMITTER | N2 TO Flare | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C | 1" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-6 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2212C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 4C |  |  |  | Serial link | UCP-2101C | DCS
34 | PI-2200C | PT-2200C | A | PRESSURE TRANSMITTER | ON LUBRICATOR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-10 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PI-2200C |  | PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | DCS
35 | LI-2200C | LT-2200C | A | LEVEL TRANSMITTER | ON CRANK CASE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-425 | mmH2O |  |  |  |  | ZONE2, IIB, T4
|  | LI-2200C |  | LEVEL INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | DCS
36 | FI-2206C | FT-2206C | A | FLOW TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 6C | 2" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-8710 0.2 | m3/h Barg |  |  |  |  | ZONE2, IIB, T4
|  | FI-2206C |  | FLOW INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 6C |  |  |  | Serial link | UCP-2101C | DCS
37 | TI-2204C | TT-2204C | A | TEMPERATURE TRANSMITTER | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 4" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
|  | TI-2204C |  | TEMPERATURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | DCS
38 | PDI-2204C | PDT-2204C | A | DIFF. PRESSURE TRANSMITTER | LUBE OIL FILTER | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | 1" |  |  | AI | JBU-A-2104C | UCP-2101C | 24VDC | - | 4-20mA Hart | IS |  | 0-1 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PDI-2204C |  | DIFF. PRESSURE INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | Serial link | UCP-2101C | DCS
39 | ZI-2200C | ZT-2200C | A | ROD DROP TRANSMITTER | LEFT Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2102C | UCP-2101C | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2200C |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
40 | ZI-2201C | ZT-2201C | A | ROD DROP TRANSMITTER | Right Cylinder Rod Drop Detector | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2102C | UCP-2101C | 24VDC | - | 4-20mA | IS |  | 4 | mm |  |  |  |  | ZONE2, IIB, T4
|  | ZI-2201C |  | ROD DROP INDICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
41 | XI-2200C | XT-2200C | A | Key Phasor | Key Phasor | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AI | JBU-A-2102C | UCP-2101C | 24VDC | - | 4-20mA | IS |  | 1000 | Rpm |  |  |  |  | ZONE2, IIB, T4
|  | XI-2200C |  | Key Phasor |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
42 | TI-2214C | TT-2214C | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2214C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
43 | TI-2215C | TT-2215C | A | TEMPERATURE TRAMSMITTER | Main Motor Bearing | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2215C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
44 | TI-2216C | TT-2216C | A | TEMPERATURE TRANSMITTER | Com DE Bearing Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2216C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
45 | TI-2217C | TT-2217C | A | TEMPERATURE TRANSMITTER | Comp Packing RIGHT Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC |  | 4-20mA Hart | IS |  | 0-200 | °C
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2217C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
46 | TI-2218C | TT-2218C | A | TEMPERATURE TRANSMITTER | Com NDE Bearing Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2218C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
47 | TI-2219C | TT-2219C | A | TEMPERATURE TRANSMITTER | Comp Packing LEFT Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2219C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
48 | TI-2220C | TT-2220C | A | TEMPERATURE TRANSMITTER | Com Mid Bearing Temp | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TI-2220C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
49 | TI-2221C | TT-2221C | A | TEMPERATURE TRANSMITTER | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA Hart | IS |  | 0-120 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TT-2221C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | Serial link | UCP-2101C | DCS
50 | VI-2200C | VT-2200C | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | VI-2200C |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
51 | VI-2201C | VT-2201C | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | VI-2201C |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
52 | VI-2202C | VT-2202C | A | VIBRATION TRANSMITTER | FRAME VIBRATION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | _ | JBU-A-2103C | Trip Relay UCP A | 24VDC | - | 4-20mA | IS |  | 25.4 | mm/SEC , RMS |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC
|  | VI-2202C |  | VIBRATION INDICATING |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
53 | TI-2222C | TE-2222C | A | RTD THERMO ELEMENT | MAIN MOTOR R-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC |  |  | 4-20mA
|  | TI-2222C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
54 | TI-2225C | TE-2225C | A | RTD THERMO ELEMENT | MAIN MOTOR S-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC |  |  | 4-20mA
|  | TI-2225C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
55 | TI-2228C | TE-2228C | A | RTD THERMO ELEMENT | MAIN MOTOR T-PHASE WINDING TEMP. | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | - | M-2101-A Motor Aux JB | Trip Relay UCP A | 24VDC | - | RTD | NIS |  | 0-200 | °C |  |  |  |  | ZONE2, IIB, T4
[6 empty] | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | AIRF | Trip Relay UCP A | UCP-2101C PLC |  |  | 4-20mA
|  | TI-2228C |  | TEMPERATURE INDICATION |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | Serial link | UCP-2101C | DCS
56 | TI-2191C | TS-2191C | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 1ST STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | JBU-D-2101C | Trip Relay UCP A | 24VDC |  | NC | NIS |  | 150 | °C
|  | TAHH-2191C |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | DIRF | Trip Relay UCP A | UCP-2101C PLC | 24VDC
|  | TAHH-2191C |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
57 | TI-2194C | TS-2194C | A | TEMPERATURE SWITCH | ON DISCHARGE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | NIS |  | 170 | °C
|  | TAHH-2194C |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C PLC
|  | TAHH-2194C |  | TEMPERATURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
58 | PI-2133C | PS-2133C | A | PRESSURE SWITCH | ON DISCHARGE LINE SNUBBER 2ND STAGE | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | 6" |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | NIS |  | 57 | BARG
|  | PAHH-2133C |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C PLC
|  | PAHH-2133C |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 1C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
59 | PI-2204C | PS-2204C | A | PRESSURE SWITCH | LUBE OIL FILTER DOWNSTREAM | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | N'IS |  | 1.2 | BARG |  |  |  |  | ZONE2, IIB, T4
|  | PAHH-2204C |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C PLC
|  | PAHH-2204C |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
60 | PI-2220C | PS-2220C | A | PRESSURE SWITCH | WATER TO CYLINDERS | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | 2" |  |  | - | JBU-D-2101C | Trip Relay UCP A |  |  |  | NIS |  | 2 | BARG
|  | PAHH-2220C |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIRF | Trip Relay UCP A | UCP-2101C PLC
|  | PAHH-2220C |  | PRESSURE ALARM HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
61 | XSS-2200C | XSS-2200C | A | START COMMAND HEATER LUBRICATOR | HEATER ON LUBRICATOR | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
62 | XSP-2200C | XSP-2200C | A | STOP COMMAND HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
63 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
64 | XR-2200C | XR-2200C | A | RUNNING STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
65 | XF-2200C | XF-2200C | A | FAILURE STATUS HEATER LUBRICATOR |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
66 | XSS-2201C | XSS-2201C | A | START COMMAND LUBRICATOR. OIL PUMP | LUBRICATOR. OIL PUMP (2101-LP C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
67 | XSP-2201C | XSP-2201C | A | STOP COMMAND LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
68 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
69 | XR-2201C | XR-2201C | A | RUNNING STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
70 | XF-2201C | XF-2201C | A | FAILURE STATUS LUBRICATOR. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
71 | XSS-2202C | XSS-2202C | A | START COMMAND AUX. OIL PUMP | AUX. OIL PUMP (P-2101-AP C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XSP-2202C | XSP-2202C | A | STOP COMMAND AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
73 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
74 | XR-2202C | XR-2202C | A | RUNNING STATUSAUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
72 | XF-2202C | XF-2202C | A | FAILURE STATUS AUX. OIL PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
75 | XSP-2203C | XSP-2203C | A | START COMMAND HEATER CRANK CASE | HEATER CRANK CASE(H-2101-OH C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
76 | XSS-2203C | XSS-2203C | A | STOP COMMAND HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
77 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
78 | XR-2203C | XR-2203C | A | RUNNING STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
79 | XF-2203C | XF-2203C | A | FAILURE STATUS HEATER CRANK CASE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
80 | XSS-2205C | XSS-2205C | A | START COMMAND LUB OIL COOLER MOTOR A | LUB OIL COOLER (AE-2101-OC C1) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
81 | XSP-2205C | XSP-2205C | A | STOP COMMAND LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
82 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
83 | XR-2205C | XR-2205C | A | RUNNING STATUS LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
84 | XF-2205C | XF-2205C | A | FAILURE STATUS LUB OIL COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
85 | XSS-2206C | XSS-2206C | A | START COMMAND LUB OIL COOLER MOTOR B | LUB OIL COOLER (AE-2101-OC C2) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
86 | XSP-2206C | XSP-2206C | A | STOP COMMAND LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
87 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
88 | XR-2206C | XR-2206C | A | RUNNING STATUS LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
89 | XF-2206C | XF-2206C | A | FAILURE STATUS LUB OIL COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
90 | XSS-2220C | XSS-2220C | A | START COMMAND WATER CONSULE COOLER MOTOR A | WATER CONSULE COOLER (AE-2101-WC C1) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
91 | XSP-2220C | XSP-2220C | A | STOP COMMAND WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
92 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
93 | XR-2220C | XR-2220C | A | RUNNING STATUS WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
94 | XF-2220C | XF-2220C | A | FAILURE STATUS WATER CONSULE COOLER MOTOR A |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
95 | XSS-2220C | XSS-2220C | A | START COMMAND WATER CONSULE COOLER MOTOR B | WATER CONSULE COOLER (AE-2101-WC C2) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
96 | XSP-2220C | XSP-2220C | A | STOP COMMAND WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
97 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
98 | XR-2220C | XR-2220C | A | RUNNING STATUS WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
99 | XF-2220C | XF-2220C | A | FAILURE STATUS WATER CONSULE COOLER MOTOR B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
100 | XSS-2221C | XSS-2221C | A | START COMMAND AUX WATER PUMP | AUX WATER PUMP (P-2101-AX C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
101 | XSP-2221C | XSP-2221C | A | STOP COMMAND AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
102 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
103 | XR-2221C | XR-2221C | A | RUNNING STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
104 | XF-2221C | XF-2221C | A | FAILURE STATUS AUX WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
105 | XSS-2222C | XSS-2222C | A | START COMMAND MAIN WATER PUMP | MAIN WATER PUMP (P-2101-WP C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
106 | XSP-2222C | XSP-2222C | A | STOP COMMAND MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
107 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
108 | XR-2222C | XR-2222C | A | RUNNING STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
109 | XF-2222C | XF-2222C | A | FAILURE STATUS MAIN WATER PUMP |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
110 | XSS-2223C | XSS-2223C | A | START COMMAND HEATER WATER CONSULE | WATER CONSULE COOLER HEATER (H-2101-WHC) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
111 | XSP-2223C | XSP-2223C | A | STOP COMMAND HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
112 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
113 | XR-2223C | XR-2223C | A | RUNNING STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
114 | XF-2223C | XF-2223C | A | FAILURE STATUS HEATER WATER CONSULE |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
115 | XSS-2224C | XSS-2224C | A | START COMMAND | MAKE UP GAS COMPRESSOR MAIN MOTOR (M-2101-C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
116 | XSP-2224C | XSP-2224C | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
117 | USD-I-60C | USD-I-60C | A | Trip Relay Center in UCP Internal USD |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  |  | Trip Relay UCP A | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
118 | XR-2224C | XR-2224C | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
119 | XF-2224C | XF-2224C | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
120 | XSS-2225C | XSS-2225C | A | START COMMAND | MOTOR BEARING DEVICE MOTOR (M-2101-BM-C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
121 | XSP-2225C | XSP-2225C | A | STOP COMMAND |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DOR | UCP-2101C | MCC | 24VDC | D | NC | NIS | [7 empty] | ZONE2, IIB, T4
122 | XR-2225C | XR-2225C | A | RUNNING STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
123 | XF-2225C | XF-2225C | A | FAULT STATUS |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | MCC | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
-
124 |  | HST-2203C | A | PUSH BUTTON | OIL HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
125 |  | HSP-2203C | A | PUSH BUTTON | OIL HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
126 |  | HSL-2203C | A | SELECTOR SWITCH | OIL HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
127 |  | HSR-2203C | A | SELECTOR SWITCH | OIL HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
128 |  | HST-2202C | A | PUSH BUTTON | AUX. LUBE OIL PUMP START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
129 |  | HSP-2202C | A | PUSH BUTTON | AUX. LUBE OIL PUMP STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
130 |  | HSL-2202C | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
131 |  | HSR-2202C | A | SELECTOR SWITCH | AUX. LUBE OIL PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
132 |  | HST-2200C | A | PUSH BUTTON | LUBRICATOR HEATER ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
133 |  | HSP-2200C | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
134 |  | HSL-2200C | A | SELECTOR SWITCH | LUBRICATOR HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
135 |  | HSR-2200C | A | SELECTOR SWITCH | LUBRICATOR HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
136 |  | HST-2201C | A | PUSH BUTTON | LUBRICATOR MOTOR ON PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
137 |  | HSP-2201C | A | PUSH BUTTON | LUBRICATOR HEATER OFF PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
138 |  | HSL-2201C | A | SELECTOR SWITCH | LUBRICATOR MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
139 |  | HSR-2201C | A | SELECTOR SWITCH | LUBRICATOR MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
140 |  | HST-2224C | A | PUSH BUTTON | MAIN MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
141 |  | HSP-2224C | A | PUSH BUTTON | MAIN MOTOR STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
142 |  | HSL-2224C | A | SELECTOR SWITCH | MAIN MOTOR LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
143 |  | HSR-2224C | A | SELECTOR SWITCH | MAIN MOTOR REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
144 |  | HST-2205C | A | PUSH BUTTON | OIL COOLER MOTOR A START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
145 |  | HSP-2205C | A | PUSH BUTTON | OIL COOLER MOTOR A STOP PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
146 |  | HSL-2205C | A | SELECTOR SWITCH | OIL COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
147 |  | HSR-2205C | A | SELECTOR SWITCH | OIL COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
148 |  | HST-2222C | A | PUSH BUTTON | MAIN WATER PUMP MOTOR START PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
149 |  | HSP-2222C | A | PUSH BUTTON | MAIN WATER PUMP MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
150 |  | HSL-2222C | A | SELECTOR SWITCH | MAIN WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
151 |  | HSR-2222C | A | SELECTOR SWITCH | MAIN WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
152 |  | HSL-2221C | A | SELECTOR SWITCH | AUX WATER PUMP LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
153 |  | HST-2221C | A | PUSH BUTTON | AUX WATER PUMP MOTOR START PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
154 |  | HSP-2221C | A | PUSH BUTTON | AUX WATER PUMP MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
155 |  | HSL-2221C | A | SELECTOR SWITCH | AUX WATER PUMP REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
156 |  | HSR-2221C | A | PUSH BUTTON | WATER HEATER ON PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
157 |  | HSL-2221C | A | PUSH BUTTON | WATER HEATER OFF PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
158 |  | HSL-2223C | A | SELECTOR SWITCH | WATER HEATER LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
159 |  | HSR-2223C | A | SELECTOR SWITCH | WATER HEATER REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
160 |  | HST-2223C | A | PUSH BUTTON | WATER COOLER MOTOR A START PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
161 |  | HSP-2223C | A | PUSH BUTTON | WATER COOLER MOTOR A STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
162 |  | HSL-2220C | A | SELECTOR SWITCH | WATER COOLER MOTOR A LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
163 |  | HSR--2220C | A | SELECTOR SWITCH | WATER COOLER MOTOR A REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
164 |  | HST--2225C | A | PUSH BUTTON | BARRING MOTOR START PUSHBUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
165 |  | HSP--2225C | A | PUSH BUTTON | BARRING MOTOR STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
166 |  | HST-2206C | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
167 |  | HSP-2206C | A | PUSH BUTTON | OIL COOLER MOTOR B | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DI | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
168 |  | HSL-2206C | A | SELECTOR SWITCH | OIL COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
169 |  | HSR-2206C | A | SELECTOR SWITCH | OIL COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
170 |  | HST-2226C | A | PUSH BUTTON | WATER COOLER MOTOR B START PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
171 |  | HSP-2226C | A | PUSH BUTTON | WATER COOLER MOTOR B STOP PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
172 |  | HSL-2226C | A | SELECTOR SWITCH | WATER COOLER MOTOR B LOCAL SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
173 |  | HSR--2226C | A | SELECTOR SWITCH | WATER COOLER MOTOR B REMOTE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
174 |  | HSL-2241C | A | SELECTOR SWITCH | COMP LOCAL MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
175 |  | HSR-2241C | A | SELECTOR SWITCH | COMP REMOTE MODE SELECTOR SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
176 |  | HSR-2243C | A | PUSH BUTTON | RESET PUSH BUTTON | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
177 |  | HST-2241C | A | PUSH BUTTON | LAMP TEST PUSH BUTTON SWITCH | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DI | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
178 |  | ESDL-2245C | A | PUSH BUTTON | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DIRF | LCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
179 |  | HSL-2242C1 | A | SELECTOR SWITCH | LOAD 0% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DIR | UCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
180 |  | HSL-2242C2 | A | SELECTOR SWITCH | LOAD 25% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DIR | UCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
181 |  | HSL-2242C3 | A | SELECTOR SWITCH | LOAD 50% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DIR | UCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
182 |  | HSL-2242C4 | A | SELECTOR SWITCH | LOAD 75% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DIR | UCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
183 |  | HSL-2242C5 | A | SELECTOR SWITCH | LOAD 100% | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DIR | UCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
184 |  | XL-2203C | A | SIGNAL LAMP | OIL HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
185 |  | XL-2202C | A | SIGNAL LAMP | AUX LUBE OILPUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
186 |  | XL-2200C | A | SIGNAL LAMP | LUBRICATOR HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DO | UCP-2101C | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
187 |  | XL-2201C | A | SIGNAL LAMP | LUBRICATOR MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DO | UCP-2101C | LCP | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
188 |  | XL-2224C | A | SIGNAL LAMP | MAIN MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
189 |  | XL-2205C | A | SIGNAL LAMP | OIL COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
190 |  | XL-2222C | A | SIGNAL LAMP | MAIN WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
191 |  | XL-2221C | A | SIGNAL LAMP | AUX WATER PUMP MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
192 |  | XL-2223C | A | SIGNAL LAMP | WATER HEATER RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
193 |  | XL-2220C | A | SIGNAL LAMP | WATER COOLER MOTOR A RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
194 |  | XL-2225C | A | SIGNAL LAMP | BARRING MOTOR RUNNING LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 7C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
195 |  | XL-2206C | A | SIGNAL LAMP | OIL COOLER MOTOR B RUNNING | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 3C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
196 |  | XL-2226C | A | SIGNAL LAMP | WATER COOLER B RUNNING | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
197 |  | XSP-2245C | A | SIGNAL LAMP | COMP START PERMISSION | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
198 |  | XF-2245C | A | SIGNAL LAMP | COMMON ALARM LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
199 |  | ESDL-2245C | A | SIGNAL LAMP | COMMON SHUTDOWN LAMP | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C | - | - | - | DO | UCP-2101C | LCP-2101C | 24VDC | W | NO | NIS | [7 empty] | ZONE2, IIB, T4
200 |  | ESDR2-C-2101-A | A | TRIP COMMAND | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIRF | ESD | UCP-2101C | 24VDC | W | 24VDC | NIS
201 |  | ESDR2-C-2101-A | A | TRIP COMMAND | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIRF | ESD | UCP-2101C | 24VDC | W | 24VDC | NIS
202 |  | ESD2C-C-2101-A | A | TRIP FEEDBACK | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DORF | UCP-2101C | ESD | 24VDC | D | 24VDC | NIS
203 |  | ESD2-C-2101-A | A | TRIP FEEDBACK | ESD | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DORF | UCP-2101C | ESD | 24VDC | D | 24VDC | NIS
204 |  | PI-2121C | A | SPILL BACK | SPILL BACK | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | AIR | DCS | UCP-2101C | 24VDC | - | 4-20mA | NIS |  | BY CLIENT | BARG
205 |  | XS-2100C | A | Time Syc |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DI | DCS | UCP-2101C | 24VDC | W | 24VDC | NIS
206 |  | XSS-2123C | A | Permission to star |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DIR | DCS | UCP-2101C | 24VDC | W | 24VDC | NIS
207 |  | XSS-2124C | A | Ready to Start |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DO | UCP-2101C | DCS | 24VDC | D | 24VDC | NIS
208 |  | XR-2124C | A | Running Status |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-PEDCO-120-PR-PI-0011-SHEET 1C |  |  |  | DO | UCP-2101C | DCS | 24VDC | D | 24VDC | NIS
209 |  | HSS-2126C | A | Request start Permission |  | PACKAGE COMPRESSOR C-2101 A | BK-GCS-HY-120-PR-PI-0001-SHEET 9C |  |  |  | DO | UCP-2101C | FCS | 24VDC | D | 24VDC | NIS
210 |  | HST-2243C | A | COMPRESSOR START P.B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 9C |  |  |  | DI | UCP-2101C | UCP-2101C | 24VDC | D | 24VDC | NIS
211 |  | HSP-2243C | A | COMPRESSOR STOP P.B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 9C |  |  |  | DI | UCP-2101C | UCP-2101C | 24VDC | D | 24VDC | NIS
212 |  | HSR-2243C | A | COMPRESSOR RESET P.B |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 9C |  |  |  | DI | UCP-2101C | UCP-2101C | 24VDC | D | 24VDC | NIS
213 |  | ESD-2231C | A | EMERGENCY SHUT DOWN P.B | EMERGENCY SHUT DOWN | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 8C |  |  |  | DIRF | UCP-2101C | UCP-2101C | 24VDC | D | NO | NIS | [7 empty] | ZONE2, IIB, T4
214 | VI-2205C | VS-2205C | A | VIBRATION SWITCH | LUB OIL COOLER (AE-2101-OC C1) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIR | JBU-D-2102C | UCP-2101C |  |  |  | NIS
|  | VAHH-2205C |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
215 | VI-2206C | VS-2206C | A | VIBRATION SWITCH | LUB OIL COOLER (AE-2101-OC C2) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIR | JBU-D-2102C | UCP-2101C |  |  |  | NIS
|  | VAHH-2206C |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
216 | VI-2207C | VS-2207C | A | VIBRATION SWITCH | WATER CONSULE COOLER (AE-2101-WC C1) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIR | JBU-D-2102C | UCP-2101C |  |  |  | NIS
|  | VAHH-2207C |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
217 | VI-2208C | VS-2208C | A | VIBRATION SWITCH | WATER CONSULE COOLER (AE-2101-WC C2) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIR | JBU-D-2102C | UCP-2101C |  |  |  | NIS
|  | VAHH-2208C |  | VIBRATION SWITCH HIGH HIGH |  | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C | - | - | - | Serial link | UCP-2101C | DCS | 24VDC
218 | XZSO-2225C | XZSO-2225C | A | BEARING DEVICE LIMIT SWITCH FEEDBACK | BEARING DEVICE (C-2101-BD C) | PACKAGE COMPRESSOR C-2101C | BK-GCS-HY-120-PR-PI-0001-SHEET 5C |  |  |  | DIR | JBU-D-2102C | UCP-2101C |  |  |  | NIS
I/O Summery
|  |  | Num | Signal type | Quantity | 20% Spare | Total
|  |  | 1 | AI | 28 | 5.6 | 34
|  |  | 2 | AIR | 6 | 1.2 | 8
|  |  | 3 | AIRF | 14 | 2.8 | 17
|  |  | 4 | AOR | 1 | 1 | 2
|  |  | 5 | DI | 86 | 17.2 | 104
|  |  | 6 | DIR | 11 | 2.2 | 13
|  |  | 7 | DIRF | 9 | 1.8 | 11
|  |  | 8 | DO | 19 | 3.8 | 23
|  |  | 9 | DOR | 26 | 5.2 | 32
|  |  | 10 | DORF | 8 | 1.6 | 10
Note on B177: Forouzandeh Fatemeh: ALARM L,H چک شود
Note on C177: Forouzandeh Fatemeh: ALARM L,H چک شود
03