## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-HY-120-EL-DS-0002_V01 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-SVTR-HY-0031 |  |  | Transmital Date: 2025/02/01
Document Title: Datasheet (W/Drawing) For Auxiliary Motors |  |  |  |  | PEDCO Tr. No.: BK-HD-PEDCO-SVTR-HY-0031 |  |  | Transmital Date:
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-EL-DS-0002_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | ديتا شيت تمامي موتورهاي قيد شده در مدرك Electrical/Ups Consumption Load List ميبايست در اين مدرك ارائه گردد. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | ملاحظه گردید. |  |  | Not Acceptable, See item 6 bellow
2 | پيرو بند 1 صورتجلسه مورخ 1402/12/16 (صورتجلسه پيوست) مدارك مربوط به كاتالوگ و EX and IP Certificate به همراه ديتا شيت ميبايست ارائه گردد. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | به مدرک اضافه گردید. |  |  | See Item 8, 9 Bellow
3 | ماكزيمم دماي قيد شده در رديف شماره 8 ديتا شيت مطابق با دماي مورد نياز پروژه (55 درجه) در تناقض ميباشد. لذا اصلاحات لازم در رديف هاي مربوطه صورت پذيرد. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | اصلاح گردید. |  |  | Noted, Closed
4 | درج N/A در برخي از رديف ها قابل پذيرش نميباشد و ميبايست مطابق با اطلاعات سازنده تكميل گردد كه در ذيل به چند نمونه از آن اشاره شده است. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | موارد تکمیل و مشخص گردید. |  |  | Noted, Closed
4-1 | با توجه به اينكه موتورها با درجه حفاظت ضد انفجار ميباشند لذا گواهينامه هاي مربوط به آن ميبايست ارائه گردد (رديف شماره 25 ديتا شيت). درج N/A در رديف هاي مربوط به آن قابل پذيرش نميباشد. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | ارائه گردید. |  |  | Noted, Closed
4-2 | رديف هاي مربوط به Derating دمايي و ارتفاعي (رديف هاي 27 و 28 ديتا شيت) ميبايست توسط وندور تكميل گردد. درج N/A قابل پذيرش نميباشد. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | تکمیل گردید. |  |  | Noted, Closed
4-3 | رديف شماره 90 مربوط به سطح اتصال كوتاه كه ميبايست توسط وندور تاييد گردد. درج N/A قابل پذيرش نميباشد. |  | BK-SUR-ENG-MEC-02-08103 | 2023-07-19 | ترمینال باکس حفاظتی در برابر جریان اتصال کوتاه ندارد. |  |  | Noted, Closed
5 |  |  | MOM | 2023-03-07 | به نحو مقتضی اعمال گردید |  |  | from the electrical point of view Noted, Closed
6 | Data sheet for following auxiliary motors shall be added to this document: - Auxiliary oil pump P-2101-AP A/B/C - Lube oil Cooler AE-2101-OC A/B/C - Main water pump P-2101-WP A/B/C - Auxiliary water pump P-2101-Ax A/B/C - Water air cooler AE-2101-WC A/B/C |  | BK-SUR-ENG-MEC-02-08605 | 15/10/2023 | It will be added to document in next revision. the remaining items are as follows: - Lube. Oil Cooler # M-2101-OC A1/A2/B1/B2/C1/C2 - Water Console Cooler Motor # M-2101-WC A1/A2/B1/B2/C1/C2
7 | Mentioned tag number in data sheet is not same as tag number in the P&ID. For example lubricator motor tag number in the P&ID is M-2101 LP A/B/C but in the data sheet it is M-101/A/B/C. tag numbers shall be as per P&ID. |  | BK-SUR-ENG-MEC-02-08605 | 15/10/2023 | Noted and modified.
8 | Issued terminal box drawing is valid for motor with frame size 132 but as per issued data sheet, used motors for lubricating motors are 112M and for bearing device motors is 80, please clarify. |  | BK-SUR-ENG-MEC-02-08605 | 15/10/2023 | Noted.
9 | issued general arrangement drawing number and terminal box drawing number are not exist in the isuued certificate annex table, please clarify. |  | BK-SUR-ENG-MEC-02-08605 | 15/10/2023 | Noted and modified.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: H.Mozaffari Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 15/10/2023 |  |  |  |  | Date: