## COVER
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  |  | INSTRUMENT CABLE LIST | [10 empty] | شماره صفحه: 1 از 11
|  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI | 0003 | V08
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT CABLE LIST نگهداشت و افزایش تولید میدان نفتی بینک
V08 |  | Jan.2025 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V07 |  | NOV.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V06 |  | Agus.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | M.SADEGHIAN
V05 |  | Jun.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | M.SADEGHIAN
V04 |  | Apr.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V03 |  | Feb.2024 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V02 |  | NOV.2023 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V01 |  | OCT.2023 |  | AFC |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
V00 |  | SEP.2023 |  | IFR |  |  |  | Havayar Co. |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
CLIENT Doc. Number:
status:
IFA: Issued For Approval
IFR: Issued For Review
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  |  | INSTRUMENT CABLE LIST | [12 empty] | شماره صفحه:2 از 11
|  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال |  | نسخه
9184 – 073 - 053 |  |  | BK |  | GCS | HY | 120 |  | IN | LI |  | 0003 |  | V08
REVISION RECORD SHEET
Page | V00 | V01 |  | V02 |  | V03 |  | V04 |  |  | Page |  | V05 |  | V06 |  | V07 | V08
1 | X | X |  | X |  | X |  | X |  |  | 1 |  | X |  | X |  | X | X
2 | X | X |  | X |  | X |  | X |  |  | 2 |  | X |  | X |  | X | X
3 | X | X |  | X |  | X |  | X |  |  | 3 |  | X |  | X |  | X | X
4 | X | X |  | X |  | X |  | X |  |  | 4 |  | X |  | X |  | X | X
5 | X | X |  | X |  | X |  | X |  |  | 5 |  | X |  | X |  | X | X
6 | X | X |  | X |  | X |  | X |  |  | 6 |  | X |  | X |  | X | X
7 | X | X |  | X |  | X |  | X |  |  | 7 |  | X |  | X |  | X | X
8 | X | X |  | X |  | X |  | X |  |  | 8 |  | X |  | X |  | X | X
9 | [7 empty] | X |  |  | 9 |  | X |  | X |  | X | X
10 | [7 empty] | X |  |  | 10 |  | X |  | X |  | X | X
11 | [7 empty] | X |  |  | 11 |  | X |  | X |  | X | X
12 | [10 empty] | 12
13 | [10 empty] | 13
14 | [10 empty] | 14
15 | [10 empty] | 15
16 | [10 empty] | 16
17 | [10 empty] | 17
18 | [10 empty] | 18
19 | [10 empty] | 19
20 | [10 empty] | 20
21 | [10 empty] | 21
22 | [10 empty] | 22
23 | [10 empty] | 23
24 | [10 empty] | 24
25 | [10 empty] | 25
26 | [10 empty] | 26
27 | [10 empty] | 27
28 | [10 empty] | 28
29 | [10 empty] | 29
30 | [10 empty] | 30
31 | [10 empty] | 31
32 | [10 empty] | 32
33 | [10 empty] | 33
34 | [10 empty] | 34
35 | [10 empty] | 35
36 | [10 empty] | 36
37 | [10 empty] | 37
38 | [10 empty] | 38
39 | [10 empty] | 39
40 | [10 empty] | 40
41 | [10 empty] | 41
42 | [10 empty] | 42
43 | [10 empty] | 43
44 | [10 empty] | 44
45 | [10 empty] | 45
46 | [10 empty] | 46
47 | [10 empty] | 47
48 | [10 empty] | 48
49 | [10 empty] | 49
50 | [10 empty] | 50
51 | [10 empty] | 51
52 | [10 empty] | 52
53 | [10 empty] | 53
54 | [10 empty] | 54
55 | [10 empty] | 55
56 | [10 empty] | 56
57 | [10 empty] | 57
58 | [10 empty] | 58
59 | [10 empty] | 59
60 | [10 empty] | 60
61 | [10 empty] | 61
62 | [10 empty] | 62
63 | [10 empty] | 63
64 | [10 empty] | 64

## CompA
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  | INSTRUMENT CABLE LIST
|  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه:3 از11
9184 – 073 - 053 |  | BK | GCS | HY | 120 |  | IN | LI | 0003 | V08
Item No. | Cable Tag No. | From | To |  | Cable size | Description |  |  | Color | Cable Length (m) | Gland | IS/NIS | Remark
1 | IC-C-PSOV-2201A | C-JBU-S-2101A | C-PSOV-2201A |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
2 | IC-C-PSOV-2202A |  | C-PSOV-2202A |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
3 | IC-C-PSOV-2203A |  | C-PSOV-2203A |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
4 | IC-C-PSOV-2204A |  | C-PSOV-2204A |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
5 | IC-C-PSOV-2205A |  | C-PSOV-2205A |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
6 | MC-C-JBU-S-2101A | UCP-2101A | C-JBU-S-2101A |  | 7x2x2.5mm^3 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 330 | M40 | NIS | Out of Havayar scope of work (By Hirgan)
7 | IC-PSOV-2123A | PSOV-2123A | UCP-2101A |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 350 | M20-O | NIS | Out of Havayar scope of work (By Hirgan) Direct
8 | IC-C-TS-2191A | C-TS-2191A | C-JBU-D-2101A |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
9 | IC-C-TS-2194A | C-TS-2194A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
10 | IC-C-PS-2133A | C-PS-2133A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
11 | IC-C-PS-2204A | C-PS-2204A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
12 | IC-C-PS-2220A | C-PS-2220A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
13 | MC-C-JBU-D-2101A | C-JBU-D-2101A | UCP-2101A |  | 7x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan)
14 | IC-VS-2205A | VS-2205A | C-JBU-D-2102A |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
15 | IC-VS-2206A | VS-2206A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
16 | IC-VS-2207A | VS-2207A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
17 | IC-VS-2208A | VS-2208A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
18 | IC-C-XZSO-2225A | C-XZSO-2225A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
19 | MC-C-JBU-D-2102A | C-JBU-D-2102A | UCP-2101A |  | 7x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan)
20 | IC-XZSO-2123A | XZSO-2123A | JBU-D-2103A (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 30 | M20-O | NIS | Out of Havayar scope of work (By Hirgan)
21 | IC-XZSC-2123A | XZSC-2123A | JBU-D-2103A (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 30 | M20-O | NIS | Out of Havayar scope of work (By Hirgan)
22 | MC-JBU-D-2103A | C-JBU-D-2103A | UCP-2101A |  | 7x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan
23 | IC-FT-2121A | FT-2121A | JBU-A-2101 (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
24 | IC-TT-2122A | TT-2122A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
25 | IC-PDT-2122A | PDT-2122A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
26 | IC-PT-2123A | PT-2123A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
27 | IC-TT-2123A | TT-2123A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
28 | IC-PT-2124A | PT-2124A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
29 | IC-FT-2131A | FT-2131A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
30 | IC-TT-2132A | TT-2132A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
31 | IC-PT-2132A | PT-2132A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
32 | IC-PDT-2132A | PDT-2132A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
33 | IC-TT-2133A | TT-2133A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
34 | IC-PT-2133A | PT-2133A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
35 | IC-PV-2123A | PV-2123A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
36 | IC-PYZ-2123A | PYZ-2123A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
37 | MC-JBU-A-2101 | JBU-A-2101 | UCP-2101A |  | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 380 | M50 | IS | Out of Havayar scope of work (By Hirgan)
38 | IC-C-TE-2214A | C-TE-2214A | C-TT-2214A |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
39 | IC-C-TE-2215A | C-TE-2215A | C-TT-2215A |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
40 | IC-C-TE-2216A | C-TE-2216A | C-TT-2216A |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
41 | IC-C-TE-2217A | C-TE-2217A | C-TT-22117A | TT-22117A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
42 | IC-C-TE-2218A | C-TE-2218A | C-TT-2218A | TT-2218A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
43 | IC-C-TE-2219A | C-TE-2219A | C-TT-2219A | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
44 | IC-C-TE-2220A | C-TE-2220A | C-TT-2220A | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | _ | M20-O | IS | Supply by Havayar
45 | IC-C-TE-2221A | C-TE-2220A | C-TT-2220A | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | _ | M20-O | IS | Supply by Havayar
46 | IC-C-TT-2203A | C-TT-2203A | C-JBU-A-2101A |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
47 | IC-C-TT-2213A | C-TT-2213A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
48 | IC-C-PT-2204A | C-PT-2204A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
49 | IC-C-PT-2220A | C-PT-2220A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
50 | IC-C-LT-2213A | C-LT-2213A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
51 | IC-C-TT-2191A | C-TT-2191A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
52 | IC-C-TT-2194A | C-TT-2194A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
53 | IC-C-TT-2231A | C-TT-2231A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
54 | MC-C-JBU-A-2101A | C-JBU-A-2101A | UCP-2101A |  | 12x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
55 | IC-C-PT-2201A | C-PT-2201A | C-JBU-A-2104A |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
56 | IC-C-PT-2210A | C-PT-2210A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
57 | IC-C-PT-2211A | C-PT-2211A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
58 | IC-C-PT-2212A | C-PT-2212A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
59 | IC-C-PT-2200A | C-PT-2200A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
60 | IC-C-LT-2200A | C-LT-2200A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
61 | IC-C-FT-2206A | C-FT-2206A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
62 | IC-C-TT-2204A | C-TT-2204A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
63 | IC-C-PDT-2204A | C-PDT-2204A |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
64 | MC-C-JBU-A-2104A | C-JBU-A-2104A | UCP-2101A |  | 12x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
65 | IC-C-ZE-2200A | C-ZE-2200A | C-JBU-A-2102A |  | Special cable |  |  |  | N/A | 8 | M20-O | N/A | Supply by Havayar
66 | IC-C-ZE-2201A | C-ZE-2201A |  |  | Special cable |  |  |  | N/A | 8 | M20-O | N/A | Supply by Havayar
67 | IC-C-XE-2200A | C-XE-2200A |  |  | Special cable |  |  |  | N/A | 8.5 | M20-O | N/A | Supply by Havayar
68 | MC-C-JBU-A-2102A | C-JBU-A-2102A | UCP-2101A |  | 7x3x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
69 | IC-C-TT-2214A | C-TT-2214A | C-JBU-A-2103A |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar Bearing DE
70 | IC-C-TT-2215A | C-TT-2215A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar Bearing NDE
71 | IC-C-TT-2216A | C-TT-2216A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
72 | IC-C-TT-2217A | C-TT-2217A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
73 | IC-C-TT-2218A | C-TT-2218A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
74 | IC-C-TT-2219A | C-TT-2219A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
75 | IC-C-TT-2220A | C-TT-2220A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
76 | IC-C-TT-2221A | C-TT-2221A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 20 | M20-O | IS | Supply by Havayar
77 | IC-C-VT-2200A | C-VT-2200A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
78 | IC-C-VT-2201A | C-VT-2201A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
79 | IC-C-VT-2202A | C-VT-2202A |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
80 | MC-C-JBU-A-2103A | C-JBU-A-2103A | UCP-2101A |  | 19x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 330 | M50 | IS | Out of Havayar scope of work (By Hirgan)
81 | IC-M-2101-A | M-2101-A Motor Aux JB | UCP-2101A |  | 12x3x1.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan Electrical ) Winding RTD cable
82 | MC-LCP-2101A1 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
83 | MC-LCP-2101A2 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
84 | MC-LCP-2101A3 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
85 | MC-LCP-2101A4 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
86 | MC-LCP-2101A5 | LCP-2101A | UCP-2101A | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
87 | MC-II-2234A | CLIENT MCC | MAIN MOTOR AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
88 | MC-II-2235A | CLIENT MCC | AUX OIL PUMP AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
89 | MC-II-2236A | CLIENT MCC | AUX WATER PUMP AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
90 | MC-II-2237A | CLIENT MCC | MAIN WATER PUMP AMMETER | 40-JB-DIA-352 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
91 | MC-II-2238A | CLIENT MCC | OIL COOLER MOTOR A AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
92 | MC-II-2239A | CLIENT MCC | OIL COOLER MOTOR B AMMETER | 40-JB-DIA-352 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
93 | `MC-MCC-2101A1 | Client IRP | UCP-2101A OIL HEATER Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
94 |  |  | UCP-2101A OIL HEATER Start Command | 40-JB-DIA-351
95 |  |  | UCP-2101A OIL HEATER Running Status | 40-JB-DIA-351
96 |  |  | UCP-2101A OIL HEATER Fault Status | 40-JB-DIA-351
97 |  | Client IRP | UCP-2101A AUX OIL PUMP Stop Command | 40-JB-DIA-351
98 |  |  | UCP-2101A AUX OIL PUMP Start Command | 40-JB-DIA-351
99 |  |  | UCP-2101A AUX OIL PUMP Running Status | 40-JB-DIA-351
100 |  |  | UCP-2101A AUX OIL PUMP Fault Status | 40-JB-DIA-351
101 |  | Client IRP | UCP-2101A LUBRICATOR HEATER Stop Command | 40-JB-DIA-351
102 |  |  | UCP-2101A LUBRICATOR HEATER Start Command | 40-JB-DIA-351
103 |  |  | UCP-2101A LUBRICATOR HEATER Running Status | 40-JB-DIA-351
104 |  |  | UCP-2101A LUBRICATOR HEATER Fault Status | 40-JB-DIA-351
105 | `MC-MCC-2101A2 | Client IRP | UCP-2101A LUBRICATOR MOTOR Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
106 |  |  | UCP-2101A LUBRICATOR MOTOR Start Command | 40-JB-DIA-351
107 |  |  | UCP-2101A LUBRICATOR MOTOR Running Status | 40-JB-DIA-351
108 |  |  | UCP-2101A LUBRICATOR MOTOR Fault Status | 40-JB-DIA-351
109 |  | Client IRP | UCP-2101A MAIN MOTOR Stop Command | 40-JB-DIA-351
110 |  |  | UCP-2101A MAIN MOTOR Start Command | 40-JB-DIA-351
111 |  |  | UCP-2101A MAIN MOTOR Running Status | 40-JB-DIA-351
112 |  |  | UCP-2101A MAIN MOTOR Fault Status | 40-JB-DIA-351
113 |  | Client IRP | UCP-2101A OIL COOLER MOTOR A Stop Command | 40-JB-DIA-351
114 |  |  | UCP-2101A OIL COOLER MOTOR A Start Command | 40-JB-DIA-351
115 |  |  | UCP-2101A OIL COOLER MOTOR A Running Status | 40-JB-DIA-351
116 |  |  | UCP-2101A OIL COOLER MOTOR A Fault Status | 40-JB-DIA-351
117 | `MC-MCC-2101A3 | Client IRP | UCP-2101A MAIN WATER PUMP Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
118 |  |  | UCP-2101A MAIN WATER PUMP Start Command | 40-JB-DIA-351
119 |  |  | UCP-2101A MAIN WATER PUMP Running Status | 40-JB-DIA-351
120 |  |  | UCP-2101A MAIN WATER PUMP Fault Status | 40-JB-DIA-351
121 |  | Client IRP | UCP-2101A AUX WATER PUMP Stop Command | 40-JB-DIA-351
122 |  |  | UCP-2101A AUX WATER PUMP Start Command | 40-JB-DIA-351
123 |  |  | UCP-2101A AUX WATER PUMP Running Status | 40-JB-DIA-351
124 |  |  | UCP-2101A AUX WATER PUMP Fault Status | 40-JB-DIA-351
125 |  | Client IRP | UCP-2101A WATER HEATER Stop Command | 40-JB-DIA-351
126 |  |  | UCP-2101A WATER HEATER Start Command | 40-JB-DIA-351
127 |  |  | UCP-2101A WATER HEATER Running Status | 40-JB-DIA-351
128 |  |  | UCP-2101A WATER HEATER Fault Status | 40-JB-DIA-351
129 | `MC-MCC-2101A4 | Client IRP | UCP-2101A WATER COOLER MOTOR A Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
130 |  |  | UCP-2101A WATER COOLER MOTOR A Start Command | 40-JB-DIA-351
131 |  |  | UCP-2101A WATER COOLER MOTOR A Running Status | 40-JB-DIA-351
132 |  |  | UCP-2101A WATER COOLER MOTOR A Fault Status | 40-JB-DIA-351
133 |  | Client IRP | UCP-2101A BARRING MOTOR Stop Command | 40-JB-DIA-351
134 |  |  | UCP-2101A BARRING MOTOR Start Command | 40-JB-DIA-351
135 |  |  | UCP-2101A BARRING MOTOR Running Status | 40-JB-DIA-351
136 |  |  | UCP-2101A BARRING MOTOR Fault Status | 40-JB-DIA-351
137 |  | Client IRP | UCP-2101A OIL COOLER MOTOR B Stop Command | 40-JB-DIA-351
138 |  |  | UCP-2101A OIL COOLER MOTOR B Start Command | 40-JB-DIA-351
139 |  |  | UCP-2101A OIL COOLER MOTOR B Running Status | 40-JB-DIA-351
140 |  |  | UCP-2101A OIL COOLER MOTOR B Fault Status | 40-JB-DIA-351
141 | `MC-MCC-2101A5 | Client IRP | UCP-2101A WATER COOLER MOTOR B Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
142 |  |  | UCP-2101A WATER COOLER MOTOR B Start Command | 40-JB-DIA-351
143 |  |  | UCP-2101A WATER COOLER MOTOR B Running Status | 40-JB-DIA-351
144 |  |  | UCP-2101A WATER COOLER MOTOR B Fault Status | 40-JB-DIA-351
145 | `MC-MCC-2101A6 | Client IRP | UCP-2101A Relay Trip OIL HEATER ESD Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 140 | M50 | NIS | Out of Havayar scope of work
146 |  |  | UCP-2101A Relay Trip AUX OIL PUMP ESD Command | 40-JB-DIA-351
147 |  |  | UCP-2101A Relay Trip LUBRICATOR HEATER ESD Command | 40-JB-DIA-351
148 |  |  | UCP-2101A Relay Trip LUBRICATOR MOTOR ESD Command | 40-JB-DIA-351
149 |  | Client IRP | UCP-2101A Relay Trip MAIN MOTOR ESD Command | 40-JB-DIA-351
150 |  |  | UCP-2101A Relay Trip OIL COOLER MOTOR A ESD Command | 40-JB-DIA-351
151 |  |  | UCP-2101A Relay Trip MAIN WATER PUMP ESD Command | 40-JB-DIA-351
152 |  |  | UCP-2101A Relay Trip AUX WATER PUMP ESD Command | 40-JB-DIA-351
153 |  | Client IRP | UCP-2101A Relay Trip WATER HEATER ESD Command | 40-JB-DIA-351
154 |  |  | UCP-2101A Relay Trip WATER COOLER MOTOR A ESD Command | 40-JB-DIA-351
155 |  |  | UCP-2101A Relay Trip OIL COOLER MOTOR B ESD Command | 40-JB-DIA-351
156 |  |  | UCP-2101A Relay Trip WATER COOLER MOTOR B ESD Command | 40-JB-DIA-351
157 | MC-ESD-2101A | ESD | UCP-2101A | 40-JB-DIA-351 | 12x2x1mm^2 | CU,MGT,XLPE,Wire Drain,OSC,PVC,FIRE RESISTANT |  |  | Gray Red Strip | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
158 | MC-DCS-2101A | DCS | UCP-2101A | 40-JB-DIA-351 | 12x2x1mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
159 | IC-PI-2121A | DCS | UCP-2101A | 40-JB-DIA-351 | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 330 | M20-O | NIS | Out of Havayar scope of work (By Hirgan) Spill Back

## CompB
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  | INSTRUMENT CABLE LIST
|  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه:3 از11
9184 – 073 - 053 |  | BK | GCS | HY | 120 |  | IN | LI | 0003 | V08
Item No. | Cable Tag No. | From | To |  | Cable size | Description |  |  | Color | Cable Length (m) | Gland | IS/NIS | Remark
1 | IC-C-PSOV-2201B | C-JBU-S-2101B | C-PSOV-2201B |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
2 | IC-C-PSOV-2202B |  | C-PSOV-2202B |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
3 | IC-C-PSOV-2203B |  | C-PSOV-2203B |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
4 | IC-C-PSOV-2204B |  | C-PSOV-2204B |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
5 | IC-C-PSOV-2205B |  | C-PSOV-2205B |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
6 | MC-C-JBU-S-2101B | UCP-2101B | C-JBU-S-2101B |  | 7x2x2.5mm^3 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 330 | M40 | NIS | Out of Havayar scope of work (By Hirgan)
7 | IC-PSOV-2123B | PSOV-2123B | UCP-2101B |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 350 | M20-O | NIS | Out of Havayar scope of work (By Hirgan) Direct
8 | IC-C-TS-2191B | C-TS-2191B | C-JBU-D-2101B |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
9 | IC-C-TS-2194B | C-TS-2194B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
10 | IC-C-PS-2133B | C-PS-2133B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
11 | IC-C-PS-2204B | C-PS-2204B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
12 | IC-C-PS-2220B | C-PS-2220B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
13 | MC-C-JBU-D-2101B | C-JBU-D-2101B | UCP-2101B |  | 7x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan)
14 | IC-VS-2205B | VS-2205B | C-JBU-D-2102B |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
15 | IC-VS-2206B | VS-2206B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
16 | IC-VS-2207B | VS-2207B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
17 | IC-VS-2208B | VS-2208B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
18 | IC-C-XZSO-2225B | C-XZSO-2225B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
19 | MC-C-JBU-D-2102B | C-JBU-D-2102B | UCP-2101B |  | 7x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan)
20 | IC-XZSO-2123B | XZSO-2123B | JBU-D-2103B (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 30 | M20-O | NIS | Out of Havayar scope of work (By Hirgan)
21 | IC-XZSC-2123B | XZSC-2123B | JBU-D-2103B (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 30 | M20-O | NIS | Out of Havayar scope of work (By Hirgan)
22 | MC-JBU-D-2103B | C-JBU-D-2103B | UCP-2101B |  | 7x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan
23 | IC-FT-2121B | FT-2121B | JBU-A-2102 (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
24 | IC-TT-2122B | TT-2122B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
25 | IC-PDT-2122B | PDT-2122B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
26 | IC-PT-2123B | PT-2123B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
27 | IC-TT-2123B | TT-2123B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
28 | IC-PT-2124B | PT-2124B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
29 | IC-FT-2131B | FT-2131B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
30 | IC-TT-2132B | TT-2132B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
31 | IC-PT-2132B | PT-2132B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
32 | IC-PDT-2132B | PDT-2132B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
33 | IC-TT-2133B | TT-2133B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
34 | IC-PT-2133B | PT-2133B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
35 | IC-PV-2123B | PV-2123B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
36 | IC-PYZ-2123B | PYZ-2123B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
37 | MC-JBU-A-2102 | JBU-A-2102 | UCP-2101B |  | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 380 | M50 | IS | Out of Havayar scope of work (By Hirgan)
38 | IC-C-TE-2214B | C-TE-2214B | C-TT-2214B |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
39 | IC-C-TE-2215B | C-TE-2215B | C-TT-2215B |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
40 | IC-C-TE-2216B | C-TE-2216B | C-TT-2216B |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
41 | IC-C-TE-2217B | C-TE-2217B | C-TT-22117B | TT-22117A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
42 | IC-C-TE-2218B | C-TE-2218B | C-TT-2218B | TT-2218A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
43 | IC-C-TE-2219B | C-TE-2219B | C-TT-2219B | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
44 | IC-C-TE-2220B | C-TE-2220B | C-TT-2220B | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | _ | M20-O | IS | Supply by Havayar
45 | IC-C-TE-2221B | C-TE-2220B | C-TT-2220B | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | _ | M20-O | IS | Supply by Havayar
46 | IC-C-TT-2203B | C-TT-2203B | C-JBU-A-2101B |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
47 | IC-C-TT-2213B | C-TT-2213B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
48 | IC-C-PT-2204B | C-PT-2204B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
49 | IC-C-PT-2220B | C-PT-2220B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
50 | IC-C-LT-2213B | C-LT-2213B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
51 | IC-C-TT-2191B | C-TT-2191B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
52 | IC-C-TT-2194B | C-TT-2194B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
53 | IC-C-TT-2231B | C-TT-2231B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
54 | MC-C-JBU-A-2101B | C-JBU-A-2101B | UCP-2101B |  | 12x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
55 | IC-C-PT-2201B | C-PT-2201B | C-JBU-A-2104B |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
56 | IC-C-PT-2210B | C-PT-2210B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
57 | IC-C-PT-2211B | C-PT-2211B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
58 | IC-C-PT-2212B | C-PT-2212B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
59 | IC-C-PT-2200B | C-PT-2200B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
60 | IC-C-LT-2200B | C-LT-2200B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
61 | IC-C-FT-2206B | C-FT-2206B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
62 | IC-C-TT-2204B | C-TT-2204B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
63 | IC-C-PDT-2204B | C-PDT-2204B |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
64 | MC-C-JBU-A-2104B | C-JBU-A-2104B | UCP-2101B |  | 12x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
65 | IC-C-ZE-2200B | C-ZE-2200B | C-JBU-A-2102B |  | Special cable |  |  |  | N/A | 8 | M20-O | N/A | Supply by Havayar
66 | IC-C-ZE-2201B | C-ZE-2201B |  |  | Special cable |  |  |  | N/A | 8 | M20-O | N/A | Supply by Havayar
67 | IC-C-XE-2200B | C-XE-2200B |  |  | Special cable |  |  |  | N/A | 8.5 | M20-O | N/A | Supply by Havayar
68 | MC-C-JBU-A-2102B | C-JBU-A-2102B | UCP-2101B |  | 7x3x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
69 | IC-C-TT-2214B | C-TT-2214B | C-JBU-A-2103B |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar Bearing DE
70 | IC-C-TT-2215B | C-TT-2215B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar Bearing NDE
71 | IC-C-TT-2216B | C-TT-2216B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
72 | IC-C-TT-2217B | C-TT-2217B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
73 | IC-C-TT-2218B | C-TT-2218B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
74 | IC-C-TT-2219B | C-TT-2219B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
75 | IC-C-TT-2220B | C-TT-2220B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
76 | IC-C-TT-2221B | C-TT-2221B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 20 | M20-O | IS | Supply by Havayar
77 | IC-C-VT-2200B | C-VT-2200B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
78 | IC-C-VT-2201B | C-VT-2201B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
79 | IC-C-VT-2202B | C-VT-2202B |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
80 | MC-C-JBU-A-2103B | C-JBU-A-2103B | UCP-2101B |  | 19x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 330 | M50 | IS | Out of Havayar scope of work (By Hirgan)
81 | IC-M-2101-A | M-2101-A Motor Aux JB | UCP-2101B |  | 12x3x1.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan Electrical ) Winding RTD cable
82 | MC-LCP-2101B1 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
83 | MC-LCP-2101B2 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
84 | MC-LCP-2101B3 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
85 | MC-LCP-2101B4 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
86 | MC-LCP-2101B5 | LCP-2101B | UCP-2101B | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
87 | MC-II-2234B | CLIENT MCC | MAIN MOTOR AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
88 | MC-II-2235B | CLIENT MCC | AUX OIL PUMP AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
89 | MC-II-2236B | CLIENT MCC | AUX WATER PUMP AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
90 | MC-II-2237B | CLIENT MCC | MAIN WATER PUMP AMMETER | 40-JB-DIA-352 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
91 | MC-II-2238B | CLIENT MCC | OIL COOLER MOTOR A AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
92 | MC-II-2239B | CLIENT MCC | OIL COOLER MOTOR B AMMETER | 40-JB-DIA-352 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
93 | `MC-MCC-2101B1 | Client IRP | UCP-2101B OIL HEATER Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
94 |  |  | UCP-2101B OIL HEATER Start Command | 40-JB-DIA-351
95 |  |  | UCP-2101B OIL HEATER Running Status | 40-JB-DIA-351
96 |  |  | UCP-2101B OIL HEATER Fault Status | 40-JB-DIA-351
97 |  | Client IRP | UCP-2101B AUX OIL PUMP Stop Command | 40-JB-DIA-351
98 |  |  | UCP-2101B AUX OIL PUMP Start Command | 40-JB-DIA-351
99 |  |  | UCP-2101B AUX OIL PUMP Running Status | 40-JB-DIA-351
100 |  |  | UCP-2101B AUX OIL PUMP Fault Status | 40-JB-DIA-351
101 |  | Client IRP | UCP-2101B LUBRICATOR HEATER Stop Command | 40-JB-DIA-351
102 |  |  | UCP-2101B LUBRICATOR HEATER Start Command | 40-JB-DIA-351
103 |  |  | UCP-2101B LUBRICATOR HEATER Running Status | 40-JB-DIA-351
104 |  |  | UCP-2101B LUBRICATOR HEATER Fault Status | 40-JB-DIA-351
105 | `MC-MCC-2101B2 | Client IRP | UCP-2101B LUBRICATOR MOTOR Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
106 |  |  | UCP-2101B LUBRICATOR MOTOR Start Command | 40-JB-DIA-351
107 |  |  | UCP-2101B LUBRICATOR MOTOR Running Status | 40-JB-DIA-351
108 |  |  | UCP-2101B LUBRICATOR MOTOR Fault Status | 40-JB-DIA-351
109 |  | Client IRP | UCP-2101B MAIN MOTOR Stop Command | 40-JB-DIA-351
110 |  |  | UCP-2101B MAIN MOTOR Start Command | 40-JB-DIA-351
111 |  |  | UCP-2101B MAIN MOTOR Running Status | 40-JB-DIA-351
112 |  |  | UCP-2101B MAIN MOTOR Fault Status | 40-JB-DIA-351
113 |  | Client IRP | UCP-2101B OIL COOLER MOTOR A Stop Command | 40-JB-DIA-351
114 |  |  | UCP-2101B OIL COOLER MOTOR A Start Command | 40-JB-DIA-351
115 |  |  | UCP-2101B OIL COOLER MOTOR A Running Status | 40-JB-DIA-351
116 |  |  | UCP-2101B OIL COOLER MOTOR A Fault Status | 40-JB-DIA-351
117 | `MC-MCC-2101B3 | Client IRP | UCP-2101B MAIN WATER PUMP Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
118 |  |  | UCP-2101B MAIN WATER PUMP Start Command | 40-JB-DIA-351
119 |  |  | UCP-2101B MAIN WATER PUMP Running Status | 40-JB-DIA-351
120 |  |  | UCP-2101B MAIN WATER PUMP Fault Status | 40-JB-DIA-351
121 |  | Client IRP | UCP-2101B AUX WATER PUMP Stop Command | 40-JB-DIA-351
122 |  |  | UCP-2101B AUX WATER PUMP Start Command | 40-JB-DIA-351
123 |  |  | UCP-2101B AUX WATER PUMP Running Status | 40-JB-DIA-351
124 |  |  | UCP-2101B AUX WATER PUMP Fault Status | 40-JB-DIA-351
125 |  | Client IRP | UCP-2101B WATER HEATER Stop Command | 40-JB-DIA-351
126 |  |  | UCP-2101B WATER HEATER Start Command | 40-JB-DIA-351
127 |  |  | UCP-2101B WATER HEATER Running Status | 40-JB-DIA-351
128 |  |  | UCP-2101B WATER HEATER Fault Status | 40-JB-DIA-351
129 | `MC-MCC-2101B4 | Client IRP | UCP-2101B WATER COOLER MOTOR A Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
130 |  |  | UCP-2101B WATER COOLER MOTOR A Start Command | 40-JB-DIA-351
131 |  |  | UCP-2101B WATER COOLER MOTOR A Running Status | 40-JB-DIA-351
132 |  |  | UCP-2101B WATER COOLER MOTOR A Fault Status | 40-JB-DIA-351
133 |  | Client IRP | UCP-2101B BARRING MOTOR Stop Command | 40-JB-DIA-351
134 |  |  | UCP-2101B BARRING MOTOR Start Command | 40-JB-DIA-351
135 |  |  | UCP-2101B BARRING MOTOR Running Status | 40-JB-DIA-351
136 |  |  | UCP-2101B BARRING MOTOR Fault Status | 40-JB-DIA-351
137 |  | Client IRP | UCP-2101B OIL COOLER MOTOR B Stop Command | 40-JB-DIA-351
138 |  |  | UCP-2101B OIL COOLER MOTOR B Start Command | 40-JB-DIA-351
139 |  |  | UCP-2101B OIL COOLER MOTOR B Running Status | 40-JB-DIA-351
140 |  |  | UCP-2101B OIL COOLER MOTOR B Fault Status | 40-JB-DIA-351
141 | `MC-MCC-2101B5 | Client IRP | UCP-2101B WATER COOLER MOTOR B Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
142 |  |  | UCP-2101B WATER COOLER MOTOR B Start Command | 40-JB-DIA-351
143 |  |  | UCP-2101B WATER COOLER MOTOR B Running Status | 40-JB-DIA-351
144 |  |  | UCP-2101B WATER COOLER MOTOR B Fault Status | 40-JB-DIA-351
145 | `MC-MCC-2101B6 | Client IRP | UCP-2101B Relay Trip OIL HEATER ESD Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 140 | M50 | NIS | Out of Havayar scope of work
146 |  |  | UCP-2101B Relay Trip AUX OIL PUMP ESD Command | 40-JB-DIA-351
147 |  |  | UCP-2101B Relay Trip LUBRICATOR HEATER ESD Command | 40-JB-DIA-351
148 |  |  | UCP-2101B Relay Trip LUBRICATOR MOTOR ESD Command | 40-JB-DIA-351
149 |  | Client IRP | UCP-2101B Relay Trip MAIN MOTOR ESD Command | 40-JB-DIA-351
150 |  |  | UCP-2101B Relay Trip OIL COOLER MOTOR A ESD Command | 40-JB-DIA-351
151 |  |  | UCP-2101B Relay Trip MAIN WATER PUMP ESD Command | 40-JB-DIA-351
152 |  |  | UCP-2101B Relay Trip AUX WATER PUMP ESD Command | 40-JB-DIA-351
153 |  | Client IRP | UCP-2101B Relay Trip WATER HEATER ESD Command | 40-JB-DIA-351
154 |  |  | UCP-2101B Relay Trip WATER COOLER MOTOR A ESD Command | 40-JB-DIA-351
155 |  |  | UCP-2101B Relay Trip OIL COOLER MOTOR B ESD Command | 40-JB-DIA-351
156 |  |  | UCP-2101B Relay Trip WATER COOLER MOTOR B ESD Command | 40-JB-DIA-351
157 | MC-ESD-2101B | ESD | UCP-2101B | 40-JB-DIA-351 | 12x2x1mm^2 | CU,MGT,XLPE,Wire Drain,OSC,PVC,FIRE RESISTANT |  |  | Gray Red Strip | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
158 | MC-DCS-2101B | DCS | UCP-2101B | 40-JB-DIA-351 | 12x2x1mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
159 | IC-PI-2121B | DCS | UCP-2101B | 40-JB-DIA-351 | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 330 | M20-O | NIS | Out of Havayar scope of work (By Hirgan) Spill Back

## CompC
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز (رفت و برگشتی) بینک (قرارداد BK-HD-GCS-CO-0008_03)
شماره پیمان: |  | INSTRUMENT CABLE LIST
|  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه:3 از11
9184 – 073 - 053 |  | BK | GCS | HY | 120 |  | IN | LI | 0003 | V08
Item No. | Cable Tag No. | From | To |  | Cable size | Description |  |  | Color | Cable Length (m) | Gland | IS/NIS | Remark
1 | IC-C-PSOV-2201C | C-JBU-S-2101C | C-PSOV-2201C |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
2 | IC-C-PSOV-2202C |  | C-PSOV-2202C |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
3 | IC-C-PSOV-2203C |  | C-PSOV-2203C |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
4 | IC-C-PSOV-2204C |  | C-PSOV-2204C |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
5 | IC-C-PSOV-2205C |  | C-PSOV-2205C |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
6 | MC-C-JBU-S-2101C | UCP-2101C | C-JBU-S-2101C |  | 7x2x2.5mm^3 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 330 | M40 | NIS | Out of Havayar scope of work (By Hirgan)
7 | IC-PSOV-2123C | PSOV-2123C | UCP-2101C |  | 1x2x2.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 350 | M20-O | NIS | Out of Havayar scope of work (By Hirgan) Direct
8 | IC-C-TS-2191C | C-TS-2191C | C-JBU-D-2101C |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
9 | IC-C-TS-2194C | C-TS-2194C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
10 | IC-C-PS-2133C | C-PS-2133C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
11 | IC-C-PS-2204C | C-PS-2204C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
12 | IC-C-PS-2220C | C-PS-2220C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 10 | M20-O | NIS | Supply by Havayar
13 | MC-C-JBU-D-2101C | C-JBU-D-2101C | UCP-2101C |  | 7x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan)
14 | IC-VS-2205C | VS-2205C | C-JBU-D-2102C |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
15 | IC-VS-2206C | VS-2206C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
16 | IC-VS-2207C | VS-2207C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
17 | IC-VS-2208C | VS-2208C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
18 | IC-C-XZSO-2225C | C-XZSO-2225C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 15 | M20-O | NIS | Supply by Havayar Loose item
19 | MC-C-JBU-D-2102C | C-JBU-D-2102C | UCP-2101C |  | 7x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan)
20 | IC-XZSO-2123C | XZSO-2123C | JBU-D-2103C (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 30 | M20-O | NIS | Out of Havayar scope of work (By Hirgan)
21 | IC-XZSC-2123C | XZSC-2123C | JBU-D-2103C (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 30 | M20-O | NIS | Out of Havayar scope of work (By Hirgan)
22 | MC-JBU-D-2103C | C-JBU-D-2103C | UCP-2101C |  | 7x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M32 | NIS | Out of Havayar scope of work (By Hirgan
23 | IC-FT-2121C | FT-2121C | JBU-A-2103 (Hirgan JB) |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
24 | IC-TT-2122C | TT-2122C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
25 | IC-PDT-2122C | PDT-2122C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
26 | IC-PT-2123C | PT-2123C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
27 | IC-TT-2123C | TT-2123C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
28 | IC-PT-2124C | PT-2124C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
29 | IC-FT-2131C | FT-2131C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
30 | IC-TT-2132C | TT-2132C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
31 | IC-PT-2132C | PT-2132C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
32 | IC-PDT-2132C | PDT-2132C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
33 | IC-TT-2133C | TT-2133C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
34 | IC-PT-2133C | PT-2133C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
35 | IC-PV-2123C | PV-2123C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
36 | IC-PYZ-2123C | PYZ-2123C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 30 | M20-O | IS | Out of Havayar scope of work (By Hirgan) Direct
37 | MC-JBU-A-2103 | JBU-A-2103 | UCP-2101C |  | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 380 | M50 | IS | Out of Havayar scope of work (By Hirgan)
38 | IC-C-TE-2214C | C-TE-2214C | C-TT-2214C |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
39 | IC-C-TE-2215C | C-TE-2215C | C-TT-2215C |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
40 | IC-C-TE-2216C | C-TE-2216C | C-TT-2216C |  | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
41 | IC-C-TE-2217C | C-TE-2217C | C-TT-22117C | TT-22117A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
42 | IC-C-TE-2218C | C-TE-2218C | C-TT-2218C | TT-2218A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
43 | IC-C-TE-2219C | C-TE-2219C | C-TT-2219C | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
44 | IC-C-TE-2220C | C-TE-2220C | C-TT-2220C | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | _ | M20-O | IS | Supply by Havayar
45 | IC-C-TE-2221C | C-TE-2220C | C-TT-2220C | TT-2219A | 1x3x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | _ | M20-O | IS | Supply by Havayar
46 | IC-C-TT-2203C | C-TT-2203C | C-JBU-A-2101C |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
47 | IC-C-TT-2213C | C-TT-2213C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
48 | IC-C-PT-2204C | C-PT-2204C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
49 | IC-C-PT-2220C | C-PT-2220C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
50 | IC-C-LT-2213C | C-LT-2213C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
51 | IC-C-TT-2191C | C-TT-2191C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
52 | IC-C-TT-2194C | C-TT-2194C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 20 | M20-O | IS | Supply by Havayar
53 | IC-C-TT-2231C | C-TT-2231C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
54 | MC-C-JBU-A-2101C | C-JBU-A-2101C | UCP-2101C |  | 12x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
55 | IC-C-PT-2201C | C-PT-2201C | C-JBU-A-2104C |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
56 | IC-C-PT-2210C | C-PT-2210C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
57 | IC-C-PT-2211C | C-PT-2211C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
58 | IC-C-PT-2212C | C-PT-2212C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
59 | IC-C-PT-2200C | C-PT-2200C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
60 | IC-C-LT-2200C | C-LT-2200C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
61 | IC-C-FT-2206C | C-FT-2206C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
62 | IC-C-TT-2204C | C-TT-2204C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
63 | IC-C-PDT-2204C | C-PDT-2204C |  |  | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,SWA,PVC,FLAME RETARDANT |  |  | Light Blue | 10 | M20-O | IS | Supply by Havayar
64 | MC-C-JBU-A-2104C | C-JBU-A-2104C | UCP-2101C |  | 12x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
65 | IC-C-ZE-2200C | C-ZE-2200C | C-JBU-A-2102C |  | Special cable |  |  |  | N/A | 8 | M20-O | N/A | Supply by Havayar
66 | IC-C-ZE-2201C | C-ZE-2201C |  |  | Special cable |  |  |  | N/A | 8 | M20-O | N/A | Supply by Havayar
67 | IC-C-XE-2200C | C-XE-2200C |  |  | Special cable |  |  |  | N/A | 8.5 | M20-O | N/A | Supply by Havayar
68 | MC-C-JBU-A-2102C | C-JBU-A-2102C | UCP-2101C |  | 7x3x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Light Blue | 330 | M40 | IS | Out of Havayar scope of work (By Hirgan)
69 | IC-C-TT-2214C | C-TT-2214C | C-JBU-A-2103C |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar Bearing DE
70 | IC-C-TT-2215C | C-TT-2215C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar Bearing NDE
71 | IC-C-TT-2216C | C-TT-2216C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
72 | IC-C-TT-2217C | C-TT-2217C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
73 | IC-C-TT-2218C | C-TT-2218C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
74 | IC-C-TT-2219C | C-TT-2219C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
75 | IC-C-TT-2220C | C-TT-2220C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
76 | IC-C-TT-2221C | C-TT-2221C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 20 | M20-O | IS | Supply by Havayar
77 | IC-C-VT-2200C | C-VT-2200C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
78 | IC-C-VT-2201C | C-VT-2201C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
79 | IC-C-VT-2202C | C-VT-2202C |  |  | 1x2x1.5mm^2 | CU,MGT,XLPE,Wire Drain,OSC,SWA,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 10 | M20-O | IS | Supply by Havayar
80 | MC-C-JBU-A-2103C | C-JBU-A-2103C | UCP-2101C |  | 19x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Light Blue Red Strip | 330 | M50 | IS | Out of Havayar scope of work (By Hirgan)
81 | IC-M-2101-A | M-2101-A Motor Aux JB | UCP-2101C |  | 12x3x1.5mm^2 | CU,PVC,SC,OSC,SWA,PVC,FLAME RETARDANT |  |  | Black | _ | M50 | NIS | Out of Havayar scope of work (By Hirgan Electrical ) Winding RTD cable
82 | MC-LCP-2101C1 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
83 | MC-LCP-2101C2 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
84 | MC-LCP-2101C3 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
85 | MC-LCP-2101C4 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
86 | MC-LCP-2101C5 | LCP-2101C | UCP-2101C | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 330 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
87 | MC-II-2234C | CLIENT MCC | MAIN MOTOR AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
88 | MC-II-2235C | CLIENT MCC | AUX OIL PUMP AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
89 | MC-II-2236C | CLIENT MCC | AUX WATER PUMP AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
90 | MC-II-2237C | CLIENT MCC | MAIN WATER PUMP AMMETER | 40-JB-DIA-352 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
91 | MC-II-2238C | CLIENT MCC | OIL COOLER MOTOR A AMMETER | 40-JB-DIA-351 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
92 | MC-II-2239C | CLIENT MCC | OIL COOLER MOTOR B AMMETER | 40-JB-DIA-352 | 3x2.5mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Black | 330 | M25 | NIS | Out of Havayar scope of work (By Hirgan) (By Hirgan Electrical )
93 | `MC-MCC-2101C1 | Client IRP | UCP-2101C OIL HEATER Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
94 |  |  | UCP-2101C OIL HEATER Start Command | 40-JB-DIA-351
95 |  |  | UCP-2101C OIL HEATER Running Status | 40-JB-DIA-351
96 |  |  | UCP-2101C OIL HEATER Fault Status | 40-JB-DIA-351
97 |  | Client IRP | UCP-2101C AUX OIL PUMP Stop Command | 40-JB-DIA-351
98 |  |  | UCP-2101C AUX OIL PUMP Start Command | 40-JB-DIA-351
99 |  |  | UCP-2101C AUX OIL PUMP Running Status | 40-JB-DIA-351
100 |  |  | UCP-2101C AUX OIL PUMP Fault Status | 40-JB-DIA-351
101 |  | Client IRP | UCP-2101C LUBRICATOR HEATER Stop Command | 40-JB-DIA-351
102 |  |  | UCP-2101C LUBRICATOR HEATER Start Command | 40-JB-DIA-351
103 |  |  | UCP-2101C LUBRICATOR HEATER Running Status | 40-JB-DIA-351
104 |  |  | UCP-2101C LUBRICATOR HEATER Fault Status | 40-JB-DIA-351
105 | `MC-MCC-2101C2 | Client IRP | UCP-2101C LUBRICATOR MOTOR Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
106 |  |  | UCP-2101C LUBRICATOR MOTOR Start Command | 40-JB-DIA-351
107 |  |  | UCP-2101C LUBRICATOR MOTOR Running Status | 40-JB-DIA-351
108 |  |  | UCP-2101C LUBRICATOR MOTOR Fault Status | 40-JB-DIA-351
109 |  | Client IRP | UCP-2101C MAIN MOTOR Stop Command | 40-JB-DIA-351
110 |  |  | UCP-2101C MAIN MOTOR Start Command | 40-JB-DIA-351
111 |  |  | UCP-2101C MAIN MOTOR Running Status | 40-JB-DIA-351
112 |  |  | UCP-2101C MAIN MOTOR Fault Status | 40-JB-DIA-351
113 |  | Client IRP | UCP-2101C OIL COOLER MOTOR A Stop Command | 40-JB-DIA-351
114 |  |  | UCP-2101C OIL COOLER MOTOR A Start Command | 40-JB-DIA-351
115 |  |  | UCP-2101C OIL COOLER MOTOR A Running Status | 40-JB-DIA-351
116 |  |  | UCP-2101C OIL COOLER MOTOR A Fault Status | 40-JB-DIA-351
117 | `MC-MCC-2101C3 | Client IRP | UCP-2101C MAIN WATER PUMP Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
118 |  |  | UCP-2101C MAIN WATER PUMP Start Command | 40-JB-DIA-351
119 |  |  | UCP-2101C MAIN WATER PUMP Running Status | 40-JB-DIA-351
120 |  |  | UCP-2101C MAIN WATER PUMP Fault Status | 40-JB-DIA-351
121 |  | Client IRP | UCP-2101C AUX WATER PUMP Stop Command | 40-JB-DIA-351
122 |  |  | UCP-2101C AUX WATER PUMP Start Command | 40-JB-DIA-351
123 |  |  | UCP-2101C AUX WATER PUMP Running Status | 40-JB-DIA-351
124 |  |  | UCP-2101C AUX WATER PUMP Fault Status | 40-JB-DIA-351
125 |  | Client IRP | UCP-2101C WATER HEATER Stop Command | 40-JB-DIA-351
126 |  |  | UCP-2101C WATER HEATER Start Command | 40-JB-DIA-351
127 |  |  | UCP-2101C WATER HEATER Running Status | 40-JB-DIA-351
128 |  |  | UCP-2101C WATER HEATER Fault Status | 40-JB-DIA-351
129 | `MC-MCC-2101C4 | Client IRP | UCP-2101C WATER COOLER MOTOR A Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
130 |  |  | UCP-2101C WATER COOLER MOTOR A Start Command | 40-JB-DIA-351
131 |  |  | UCP-2101C WATER COOLER MOTOR A Running Status | 40-JB-DIA-351
132 |  |  | UCP-2101C WATER COOLER MOTOR A Fault Status | 40-JB-DIA-351
133 |  | Client IRP | UCP-2101C BARRING MOTOR Stop Command | 40-JB-DIA-351
134 |  |  | UCP-2101C BARRING MOTOR Start Command | 40-JB-DIA-351
135 |  |  | UCP-2101C BARRING MOTOR Running Status | 40-JB-DIA-351
136 |  |  | UCP-2101C BARRING MOTOR Fault Status | 40-JB-DIA-351
137 |  | Client IRP | UCP-2101C OIL COOLER MOTOR B Stop Command | 40-JB-DIA-351
138 |  |  | UCP-2101C OIL COOLER MOTOR B Start Command | 40-JB-DIA-351
139 |  |  | UCP-2101C OIL COOLER MOTOR B Running Status | 40-JB-DIA-351
140 |  |  | UCP-2101C OIL COOLER MOTOR B Fault Status | 40-JB-DIA-351
141 | `MC-MCC-2101C5 | Client IRP | UCP-2101C WATER COOLER MOTOR B Stop Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FLAME RETARDANT |  |  | Gray | 140 | M50 | NIS | Out of Havayar scope of work (By Hirgan)
142 |  |  | UCP-2101C WATER COOLER MOTOR B Start Command | 40-JB-DIA-351
143 |  |  | UCP-2101C WATER COOLER MOTOR B Running Status | 40-JB-DIA-351
144 |  |  | UCP-2101C WATER COOLER MOTOR B Fault Status | 40-JB-DIA-351
145 | `MC-MCC-2101C6 | Client IRP | UCP-2101C Relay Trip OIL HEATER ESD Command | 40-JB-DIA-351 | 19x2x1mm^2 | CU,MGT,XLPE,Wire Drain,SC,OSC,SWA,Lead Sheath ,PVC,FIRE RESISTANT |  |  | Gray Red Strip | 140 | M50 | NIS | Out of Havayar scope of work
146 |  |  | UCP-2101C Relay Trip AUX OIL PUMP ESD Command | 40-JB-DIA-351
147 |  |  | UCP-2101C Relay Trip LUBRICATOR HEATER ESD Command | 40-JB-DIA-351
148 |  |  | UCP-2101C Relay Trip LUBRICATOR MOTOR ESD Command | 40-JB-DIA-351
149 |  | Client IRP | UCP-2101C Relay Trip MAIN MOTOR ESD Command | 40-JB-DIA-351
150 |  |  | UCP-2101C Relay Trip OIL COOLER MOTOR A ESD Command | 40-JB-DIA-351
151 |  |  | UCP-2101C Relay Trip MAIN WATER PUMP ESD Command | 40-JB-DIA-351
152 |  |  | UCP-2101C Relay Trip AUX WATER PUMP ESD Command | 40-JB-DIA-351
153 |  | Client IRP | UCP-2101C Relay Trip WATER HEATER ESD Command | 40-JB-DIA-351
154 |  |  | UCP-2101C Relay Trip WATER COOLER MOTOR A ESD Command | 40-JB-DIA-351
155 |  |  | UCP-2101C Relay Trip OIL COOLER MOTOR B ESD Command | 40-JB-DIA-351
156 |  |  | UCP-2101C Relay Trip WATER COOLER MOTOR B ESD Command | 40-JB-DIA-351
157 | MC-ESD-2101C | ESD | UCP-2101C | 40-JB-DIA-351 | 12x2x1mm^2 | CU,MGT,XLPE,Wire Drain,OSC,PVC,FIRE RESISTANT |  |  | Gray Red Strip | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
158 | MC-DCS-2101C | DCS | UCP-2101C | 40-JB-DIA-351 | 12x2x1mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | _ | M40 | NIS | Out of Havayar scope of work (By Hirgan)
159 | IC-PI-2121C | DCS | UCP-2101C | 40-JB-DIA-351 | 1x2x1.5mm^2 | CU,XLPE,Wire Drain,OSC,PVC,FLAME RETARDANT |  |  | Gray | 330 | M20-O | NIS | Out of Havayar scope of work (By Hirgan) Spill Back