## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No:BK-GCS-HY-120-IN-DW-0007_V01 |  |  |  |  | PEDCO Tr. No.:BK-HD-PEDCO-SVTR-HY-0115 |  |  | Transmital Date: 2025/03/10
Document Title: HOOK UP DRAWING
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-IN-DW-0007_V03 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
|  |  | 03/2294/458309 | 1403/11/15 | 1- ولوهای روی پایپینگ به صورت Socket Weld می باشد. موارد نشان داده شده Pipe هستند که در نقشه به صورت note در کنار هر ولو اضافه گردید. 2- در قسمت هایی که سایز کانکشن ابزاردقیق و ولو همسان نبود Reducing Coupling اضافه گردید. 3- در تجهیز کندانس اتفاق نمی افتد و نیازی به استفاده از Equal Tee نمی باشد. 4- گیج ها و منیفولد هم جنس نمی باشد لذا می توان مستقیما گیج به منیفولد متصل گردد. 5- اعمال گردید.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: s.akbari | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date:24 Jun 2024 |  |  |  |  | Date: