## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-HY-120-QC-PR-0003 |  |  |  |  | EPC Contractor Tr. No.: BK-HD-PEDCO-SVTR-HY-0086 |  |  | Mail Date: 2025/03/18
Document Title: SURFACE PREPARATION AND PAINTING PROCEDURE |  |  |  |  | PEDCO Tr. No.:
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-HY-120-QC-PR-0003_V02 |  |  | CRS Status: | CM
Item | Comments (Nisoc) |  | Email/letter No. | Comment Date | Clarification (By Havayar) |  |  | Client Conclusion
1 | اندازه ساینده 0.2 ال 0.5 برای رنگهای حرارتی می باشد.در خصوص سایر سامانه ها همان ابعاد 0.5 ال 1.68 مدنظر قرار گیرد. |  | 03/2294/176491 | 1403/05/10 | این مطلب در نسخه بعدی مد نظر قرار خواهد گرفت و اضافه خواهد شد.
2 | در جدول سامانه رنگ ، ردیفCompressor Body،حداکثر دمای عملیاتی ذکر نشده است.بدیهی است سامانه رنگ بر این اساس تعیین می شود. |  | 03/2294/176491 | 1403/05/10 | حداکثر دمای عملیاتی بدنه کمپرسور در نسخه جدید ذکرشده است.
3 | فام رنگ لایه های متوالی متفاوت از هم لحاظ شود. |  | 03/2294/176491 | 1403/05/10 | فام رنگ لایه های متوالی در دیتاشیتهای رنگ ذکر شده است.
4 | داده برگ رنگهای مصرفی ارایه و به تایید این امور رسانده شود. |  | 03/2294/176491 | 1403/05/10 | داده های برگ رنگهای مصرفی در نسخه جدید ارسال شده است.
5
6
7
8
9
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: | Signature |  |  |  | Clarified By:- | Signature
| Date: |  |  |  |  | Date: 3/15/2025