## Cover
نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز رفت و برگشتی بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  | CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES | [8 empty] | شماره صفحه: 1 از 11
|  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | HY |  | 120 | IN | DS | 0005 | V06
طرح نگهداشت و افزایش تولید 27 مخزن
CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES نگهداشت و افزایش تولید میدان نفتی بینک
V06 | APR. 2025 | AFC |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V05 | Nov. 2024 | AFC |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | M.SADEGHIAN
V04 | May. 2024 | AFC |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V03 | Feb. 2024 | IFR |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V02 | Oct. 2023 | IFR |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | S. Faramarzpour
V01 | Aug. 2023 | IFR |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | M.Mehrshad
V00 | Jun. 2023 | IFR |  |  |  | HAVAYAR CO |  |  | M.Fakharian |  |  |  | M.Mehrshad
Rev. | Date | Purpose of Issue/Status |  |  |  | Prepared By |  |  | Checked By |  |  |  | Approved By | Client Approval

## Index
نگهداشت و افزايش توليد ميدان نفتي بينك سطح الارض و ابنيه تحت الارض خرید پکیج های کمپرسور گاز رفت و برگشتی بینک (قرارداد BK-HD-GCS-CO-0008_03 )
شماره پیمان: 9184 – 073 - 053 |  |  |  |  | CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES | [11 empty] | شماره صفحه: 2 از 11
[5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | HY | 120 | IN | DS |  | 0005 |  | V06
Tabulation Of Revised Pages
| Page | V00 | V01 | V02 |  | V03 |  | V04 |  |  | Page |  | V05 |  | V06 |  |  | V07 | V08 | V09
| 1 | X | X | X |  | X |  | X |  |  | 1 |  | X |  | X
| 2 | X | X | X |  | X |  | X |  |  | 2 |  | X |  | X
| 3 | X | X | X |  | X |  | X |  |  | 3 |  | X |  | X
| 4 |  | X | X |  | X |  | X |  |  | 4 |  | X |  | X
| 5 | [9 empty] | 5 |  |  |  | X
| 6 | [9 empty] | 6 |  |  |  | X
| 7 | [9 empty] | 7 |  |  |  | X
| 8 | [9 empty] | 8 |  |  |  | X
| 9 | [9 empty] | 9 |  |  |  | X
| 10 | [9 empty] | 10 |  |  |  | X
| 11 | [9 empty] | 11 |  |  |  | X
| 12 | [9 empty] | 12
| 13 | [9 empty] | 13
| 14 | [9 empty] | 14
| 15 | [9 empty] | 15
| 16 | [9 empty] | 16
| 17 | [9 empty] | 17
| 18 | [9 empty] | 18
| 19 | [9 empty] | 19
| 20 | [9 empty] | 20
| 21 | [9 empty] | 21
| 22 | [9 empty] | 22
| 23 | [9 empty] | 23
| 24 | [9 empty] | 24
| 25 | [9 empty] | 25
| 26 | [9 empty] | 26
| 27 | [9 empty] | 27
| 28 | [9 empty] | 28
| 29 | [9 empty] | 29
| 30 | [9 empty] | 30
| 31 | [9 empty] | 31
| 32 | [9 empty] | 32
| 33 | [9 empty] | 33
| 34 | [9 empty] | 34
| 35 | [9 empty] | 35

## Data sheet
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گازرفت و برگشتی بینک (قرارداد BK-HD-GCS-CO-0008_03 )
CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES
شماره پیمان: 9184 – 073 - 053 | [5 empty] | Project |  | Package |  |  | Issuer |  | Facility |  | Dicipline |  |  | Doc. | Sequence |  | Rev | شماره صفحه: 3 از 11
[6 empty] | BK |  | GCS |  |  | HY |  | 120 |  | IN |  |  | DS | 0005 |  | V06
Tag Number
UCP-2101A UCP-2101B UCP-2101C | [24 empty] | UCP Data sheet
Standards and regulations
¢ | IEC | [6 empty] | ¢ | IPS | [9 empty] | £ | RITAL
Panel data
Panel type |  |  |  |  | £ | Rittal brand | [5 empty] | ¢ | Rittal type(Made in Iran) | [9 empty] | £ | Rack mounted
[5 empty] | £ | Plug-in design | [5 empty] | £ | Wall/skid Mounted
[5 empty] | £ | Fixed | [5 empty] | ¢ | Free Standing
Installation |  |  |  |  | ¢ | Indoor (Client control room) | [5 empty] | £ | Outdoor under shelter | [9 empty] | £ | Outdoor unsheltered
Color of enclosure |  |  |  |  | £ | RAL 7032 | [5 empty] | ¢ | RAL 7035 | [9 empty] | £ | Other
Dimensions |  |  |  |  | Width |  |  | As per Drawing |  |  | mm |  | Height |  |  | 2100 |  |  |  | mm |  | Depth |  |  | 800mm
Body material & size |  |  |  |  | Material |  |  | Sheet Steel |  |  | - |  | Thickness |  |  | 2 |  |  |  | mm
Door & Top material & size |  |  |  |  | Material |  |  | Sheet Steel |  |  | - |  | Thickness |  |  | 2 |  |  |  | mm
Cable connection location |  |  |  |  | ¢ | Bottom |  | £ | Top
Environmental conditions
Humidity range |  |  |  |  | £ | 0-10% |  |  | £ | 10-30% |  | £ | 30-50% |  |  | £ | 50-60% |  |  | ¢ | 60-70% |  |  | £ | 70-80%
Substation temperature (max) |  |  |  |  | £ | 25°C |  |  | £ | 30°C |  | £ | 35°C |  |  | ¢ | 43°C |  |  | £ | 44°C |  |  | £ | 50°C
Substation temperature (min) |  |  |  |  | £ | + 1 °C |  |  | ¢ | 0 °C |  | £ | -20 °C
Installation altitude above MSL |  |  |  |  | £ | sea level |  |  | ¢ | ≤1500m |  | £ | >1000m |  |  |  | >2000m
Ingress of protection |  |  |  |  | £ | IP31 |  |  | £ | IP40 |  | £ | IP41 |  |  | £ | IP42 |  |  | ¢ | IP54 |  |  | £ | IP65
Control cabinet heating / cooling |  |  |  |  | ¢ | Ventilated | [5 empty] | £ | Unventilated
[5 empty] | ¢ | Heater & Thermostat | [5 empty] | ¢ | Fan & Filter | [6 empty] | ¢ | Hydrostat |  |  |  |  | £ | None
Lighting |  |  |  |  | ¢ | Florsant | [5 empty] | ¢ | Microswitch | [6 empty] | ¢ | socket |  |  |  |  | £ | Other
Earth |  |  |  |  | ¢ | Instrument Earth (IS & NIS) | [5 empty] | ¢ | Electrical Earth
PLC data
Brand / type | [8 empty] | Siemens | [14 empty] | Other
[9 empty] | S7 - 1200 |  |  | S7-300 |  |  |  | S7- 400FH |  |  |  | Other
Redundancy | [8 empty] | No Redundancy |  |  | CPU |  |  |  | Communication |  |  |  | Powersupply |  |  |  | Critical I/O (I/O in ET200M)
HMI Type | [8 empty] | None |  |  | TP177A |  |  |  | TP177B |  |  |  | MP-277 # 19" |  |  |  | TP1500 (15")
Barrier For Analog (Hart) | [8 empty] | Yes |  |  | NO
Note1: Monitoring of machinery will be done by PLC. PLC is high available & high reliability.
Note 2: As per configuration document , ESD system is realy base included in PLC panel.
Machinery Monitoring
Rod Drop Sensor Vibration Sensor Key Phasor Temperature Sensor |  |  |  | Montoring of machinery sensor will be done by PLC.
Trip Relay Center
Analog sensor VT-PT-TT Analog Sensor RTD(Winding Main motor) |  |  |  | BARIER PHOENIX 1290774 BARIER PHOENIX 2865654 |  |  |  | Digital Signal TS-PS |  |  |  | RELAY COUPLE PHOENIX 2986957 | [6 empty] | Trip Relay Center is back up of PLC. Trip relay center will be activated with PLC failures ,
Soft ware Data for Laptop
Orginal license |  |  | Yes | No |  |  |  | Orginal software |  |  | Yes |  |  | No |  |  | Logic source |  | Yes |  | No | One Laptop(EWS)/One IPC(OWS) Yes |  |  |  |  | No
Certificate |  |  | SIL Certificate for Barrier & Relay Trip signal
Panel IP
Used Instruments | [14 empty] | Communication | [5 empty] | Other devices
no. | Qty. | instrument |  |  |  |  | Description | [8 empty] | None | [5 empty] | Control relay
Quantity of I/O module & detail drawing as per below document: BK-GCS-HY-120-IN-DG-0001 PLC WIRING DIAGRAM & TERMINAL DETAILS BK-GCS-HY-120-IN-DG-0002 CONTROL SYSTEM CABINETS AND CONSOLES LAYOUT DRAWING Reference Document: BK-GCS-HY-120-IN-DG-0002 OVERAL CONTROL/SAFETY SYSTEM CONFIGURATION DIAGRAM BK-GCS-HY-120-PR-PI-0001 P&ID Diagram BK-GCS-HY-120-IN-LI-0005 I/O List | [15 empty] | PRO-FI Bus module For DCS | [5 empty] | Annunciator
[16 empty] | Modbus RTU module For DCS | [5 empty] | Push button (Compressor Reset,Start & Stop)
[16 empty] | PLC communication (with hard wire To ESD) | [5 empty] | Load Selector switch (0%-25%-50%-75%-100%)
[16 empty] | PLC communication (with hard wire To DCS) | [5 empty] | Indicator light
[16 empty] | Hard wire for field | [5 empty] | Terminal
[16 empty] | Ethernet to IPC | [5 empty] | MCB
[15 empty] | Note: | Some Signals between UCP and DCS/ESD are hard wire. | [5 empty] | Emergency stop
Supply voltage
Supply feeder : | [8 empty] | voltage Transformator |  |  |  |  | UPS ( Redundant dlivered by client) | [5 empty] | Normal (Fan & Lighting) | [5 empty] | Other
Voltage power rate for control panel : | [8 empty] | 24V DC |  |  |  |  | 110V AC | [5 empty] | 230V AC | [5 empty] | Other
[9 empty] | 50 Hz. |  |  |  |  | 60 Hz.
Voltage power rate for Instrumentation purposes : | [8 empty] | 24V DC |  |  |  |  | 230V AC | [5 empty] | 230V AC | [5 empty] | Other
Identification / Wiring / nameplate
Label & Name plate | [8 empty] | Label |  |  |  | Name plate |  |  |  |  | Wiring tag
Language | [8 empty] | Persian |  |  |  | English |  |  |  |  | Other
Insulation material of leads | [8 empty] | PVC |  |  |  | Flame retardant
Gland data for PLC panel
Material | [8 empty] | Brass nickel plated |  |  |  |  | Brass |  |  | thermoplastic | [5 empty] | S.S |  |  | other
Ingress of protection | [8 empty] | EExe |  | Eexd |  |  | IP54 |  |  | IP66 |  |  | IP68 |  |  | other
Mechanical protection | [8 empty] | Armoured |  |  |  |  | un-Armoured

## Sheet1
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید پکیج های کمپرسور گاز رفت و برگشتی بینک (قرارداد BK-HD-GCS-CO-0008_03 )
CONTROL PANEL PARTS DATA SHEET/LICENCE LIST/ CERTIFICATES
شماره پیمان: 9184 – 073 - 053 |  |  | Project | Package | Issuer | Facility | Dicipline | Doc. | Sequence | Rev | شماره صفحه: 4 از 11
|  |  | BK | GCS | HY | 120 | IN | DS | 0005 | V06
Software & license Part list
ROW | ITEM | ORDER NO. |  |  |  | DESCRIPTION | [5 empty] | MANUFATUTRE | OWS EWS | UNIT | Total
1 | license | 6ES7658-5AX68-0YA5 |  |  |  | SIMATIC PCS 7, software, AS/OS Engineering V9.1 Floating License for 1 user E-SW, withoutSW, without docu. license key on USB flash drive, class A, 5 languages (de, en, fr, it, sp),executable in WIN 10 LTSC 2019 WIN Server 2019 for further information, see PCS 7 V9.1Readme reference HW: PCS 7 IPC bundle ******************************* content: 1xUSB | [5 empty] | SIEMENS | EWS (Laptop) | PCS | 1
2 | license | `6ES7658-2AA68-0YA0 |  |  |  | SIMATIC PCS 7, software, OS Software Single Station V9.1 (PO 100) Single License for 1 installation R-SW, without SW, without docu. license key on USB flash drive, class A, 5 languages (de, en, fr, it, sp), executable in WIN 10 LTSC 2019 for further information, see PCS 7 V9.1 Readme reference HW: PCS 7 IPC bundle ******************************* content: 1x USB | [5 empty] | SIEMENS | OWS (IPC) | PCS | 1
3 | license | 6ES7833-1CC46-0YA5 |  |  |  | SIMATIC S7, software, F Systems V6.4, Floating License for 1 user, E-SW, without software,without documentation, license key on USB flash drive, class A, 2 languages (de, en),executable in Windows 10 Enterprise 2015 LTSB, Windows 10 Enterprise 2019 LTSC, Server2016 / Server 2019, reference hardware: PC/PG *******************************content: 1x USB | [5 empty] | SIEMENS | EWS (Laptop) | PCS | 1
4 | license | 6ES7658-2XB00-0XB0 |  |  |  | SIMATIC PCS 7, software Runtime License OS (PO 1000) Single license for 1 installation R-SW, without SW, without documentation License Key on USB stick, Class A, Reference HW: PCS 7 IPC Bundle, PCS 7 Box Bundle ******************************* Content: 1x USB | [5 empty] | SIEMENS | OWS (IPC) | PCS | 1
5 | license | 6GK1716-0HB16-0AA0 |  |  |  | HARDNET-IE S7 REDCONNECT V16 including OPC server and HARDNET IE-S7 software for fail-safe S7 communication; floating license; R-SW, software + electrical manual on DVD, license key on USB stick, class A 2 languages (de, en); for Windows 7 SP1 Professional/Enterprise/Ultimat e (64 bit); Windows® 10 Professional/Enterprise (all 64 bit) version 1809, 1903; Windows® Server 2012 R2 Update (Standard Edition); Windows® Server 2016 (Standard Edition, Datacenter); Windows® Server 2019 (Standard Edition, Enterprise) . | [5 empty] | SIEMENS | OWS (IPC) | PCS | 1
6 | SOFTWARE | 6ES7833-4CC46-0YT8 |  |  |  | SIMATIC S7, software, F Systems V6.4 Update 1, Software Media Package, data storage medium without license, use only in connection with a valid license, E-SW/R-SW, software on USB flash drive, 2 languages (de, en), executable in Windows 10 Enterprise 2015 LTSB, Windows 10 Enterprise 2019 LTSC, Server 2016 / Server 2019, reference hardware: PC/PG, ******************************* content: 1x USB | [5 empty] | SIEMENS | EWS | PCS | 1
7 | SOFTWARE | 6ES7658-4XX68-0YT8 |  |  |  | SIMATIC PCS 7, software, Software Media Package V9.1 SP2 data storage medium without license use only in connection with valid license Trial License for 14 days, without liability and warranty with restricted functionality (see product info) R-SW, software on USB without documentation 5 languages (de, en, fr, it, es), executable in Windows 10 LTSC 2019 Windows Server 2019 for more information, see PCS 7 V9.1 SP2 Readme reference hardware: PCS 7 IPC bundle ******************************* content: 1x USB | [5 empty] | SIEMENS | EWS & OWS (Laptop & IPC) | PCS | 1
8 | license | 6AV2101-0AA08-0AA5 |  |  |  | SIMATIC WinCC Comfort V18, engineering software in the TIA Portal; floating license; software and documentation on DVD; license key on USB flash drive; class A; 9 languages: de,en,zh included, fr,es,it,ru,ja,ko as download; for configuration of SIMATIC Panels. please observe product release: support.industry.siemens.com entry ID: 109813587 - - content: set (2x DVD + 1x USB) | [5 empty] | SIEMENS | EWS (Laptop) | PCS | 1
One Common IPC & One Common Laptop are in Havayar scope of work & supply for 3 Trains.. Specification of Laptop/IPC will be submitted in CONTROL SYSTEM CABINETS AND CONSOLES LAYOUT DRAWING document.