## COVER
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 1 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B) نگهداشت و افزایش تولید میدان نفتی بینک
V00 |  | NOV.2024 |  |  | IFI |  |  |  |  | iDrill M.E. |  |  | M.Fakharian |  |  | M.Sadeghian
Rev. |  | Date |  |  | Purpose of Issue / Status |  |  |  |  | Prepared by: |  |  | Checked by: |  |  | Approved by: |  |  | CLIENT Approval
CLIENT Doc. Number:
status: IFA: Issued For Approval IFI: Issued For Information AFC: Approved For Construction
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 2 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
TABULATION OF REVISED PAGES
| PAGE | V00 | V01 | V02 | V03 | V04 | V05 | V06 | V07 |  |  | PAGE | V00 | V01 | V02 | V03 | V04 | V05 | V06 | V07
| 1 | [10 empty] | 36 | bar: V00
| 2 | [10 empty] | 37 | bar: V00
| 3 | [10 empty] | 38 | bar: V00
| 4 | [10 empty] | 39 | bar: V00
| 5 | [10 empty] | 40 | bar: V00
| 6 | [10 empty] | 41 | bar: V00
| 7 | [10 empty] | 42 | bar: V00
| 8 | [10 empty] | 43 | bar: V00
| 9 | [10 empty] | 44 | bar: V00
| 10 | [10 empty] | 45 | bar: V00
| 11 | [10 empty] | 46 | bar: V00
| 12 | [10 empty] | 47 | bar: V00
| 13 | [10 empty] | 48 | bar: V00
| 14 | [10 empty] | 49 | bar: V00
| 15 | [10 empty] | 50 | bar: V00
| 16 | [10 empty] | 51 | bar: V00
| 17 | [10 empty] | 52 | bar: V00
| 18 | [10 empty] | 53 | bar: V00
| 19 | [10 empty] | 54 | bar: V00
| 20 | [10 empty] | 55 | bar: V00
| 21 | [10 empty] | 56 | bar: V00
| 22 | [10 empty] | 57 | bar: V00
| 23 | [10 empty] | 58 | bar: V00
| 24 | [10 empty] | 59 | bar: V00
| 25 | [10 empty] | 60 | bar: V00
| 26 | [10 empty] | 61 | bar: V00
| 27 | [10 empty] | 62 | bar: V00
| 28 | [10 empty] | 63 | bar: V00
| 29 | [10 empty] | 64
| 30 | [10 empty] | 65
| 31 | [10 empty] | 66
| 32 | [10 empty] | 67
| 33 | [10 empty] | 68
| 34 | [10 empty] | 69
| 35 | [10 empty] | 70
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  | TABULATION OF REVISED PAGES V03: پروژه; TABULATION OF REVISED PAGES V04: بسته کاری; TABULATION OF REVISED PAGES V06: صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 3 | شماره صفحه:
053-073 -9184 |  | TABULATION OF REVISED PAGES V03: BK; TABULATION OF REVISED PAGES V04: GCS; TABULATION OF REVISED PAGES V06: IDR | 120 |  | ME | CN |  | 0003 | V00
Table of Contents
| Item | [17 empty] | Page No
| Design Data: | [17 empty] | 4
| Material of Parts: | [17 empty] | 5
| Shell Plate Design: | [17 empty] | 6
| Requirement for Impact Testing | [17 empty] | 7
| Bottom plate design: | [17 empty] | 8
| Annular plate design: | [17 empty] | 9
| Fix Roof design: | [17 empty] | 10
| Top Angle: | [17 empty] | 11
| Intermediate wind girder: | [17 empty] | 0
| Wind overturning stability: | [17 empty] | 13
| Seismic Design (APP."E") | [17 empty] | 15
| Anchor Bolt Sizing | [17 empty] | 24
| Summary | [17 empty] | 28
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  | TABULATION OF REVISED PAGES V03: پروژه; TABULATION OF REVISED PAGES V04: بسته کاری; TABULATION OF REVISED PAGES V06: صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 4 | شماره صفحه:
053-073 -9184 |  | TABULATION OF REVISED PAGES V03: BK; TABULATION OF REVISED PAGES V04: GCS; TABULATION OF REVISED PAGES V06: IDR | 120 |  | ME | CN |  | 0003 | V00
Design Data:
| ITEM | TABULATION OF REVISED PAGES V05: Description | [5 empty] | Unit
| Tank Tag. No. | TABULATION OF REVISED PAGES V05: TK-2301 A / B
| Site Location | TABULATION OF REVISED PAGES V05: IRAN- Bushehr
| Design code | TABULATION OF REVISED PAGES V05: API Standard 650, 13th Ed
| Service | TABULATION OF REVISED PAGES V05: Fire Water
| Roof Type | TABULATION OF REVISED PAGES V05: Fix Roof | Cone Roof Suported by Rafter
Applicable Annexes | bar: TABULATION OF REVISED PAGES V05
| Tank Inside Diameter | TABULATION OF REVISED PAGES V05: 13000 | [5 empty] | mm
| Shell height | TABULATION OF REVISED PAGES V05: 9500 | [5 empty] | mm
| HLL | TABULATION OF REVISED PAGES V05: 8500 | [5 empty] | mm
| LLL | TABULATION OF REVISED PAGES V05: 850 | [5 empty] | mm
| Nominal capacity | TABULATION OF REVISED PAGES V05: 1260 | [5 empty] | m3
| Working capacity | TABULATION OF REVISED PAGES V05: 1040 | [5 empty] | m3
| Design pressure | V02: Internal; TABULATION OF REVISED PAGES V05: 0 | [5 empty] | Kpa
|  | V02: External; TABULATION OF REVISED PAGES V05: 0 | [5 empty] | Kpa
| Design Liquid Level | TABULATION OF REVISED PAGES V05: ATM+Full of Water+50 H2O | [5 empty] | mm
| Design temp. | TABULATION OF REVISED PAGES V05: 85 | [5 empty] | C°
| M.D.M.T | TABULATION OF REVISED PAGES V05: AMB. | [5 empty] | C°
| Operation Temp. | TABULATION OF REVISED PAGES V05: AMB. | [5 empty] | C°
Specific gravity | bar: TABULATION OF REVISED PAGES V05
| Corrosion allowance | TABULATION OF REVISED PAGES V03: Shell; TABULATION OF REVISED PAGES V05: 1.6 | [5 empty] | mm
|  | TABULATION OF REVISED PAGES V03: Roof; TABULATION OF REVISED PAGES V05: 1.6 | [5 empty] | mm
|  | TABULATION OF REVISED PAGES V03: Bottom; TABULATION OF REVISED PAGES V05: 1.6 | [5 empty] | mm
Insulation | bar: TABULATION OF REVISED PAGES V05
| Wind velocity | TABULATION OF REVISED PAGES V05: 193.3333 | [5 empty] | Km/h
| Design wind velocity | TABULATION OF REVISED PAGES V05: 232 | [5 empty] | Km/h
Wind Exposure | bar: TABULATION OF REVISED PAGES V05
| Earthquake motion analysis | TABULATION OF REVISED PAGES V05: API 650An.E&F / ASCE 7-10
| Load code | TABULATION OF REVISED PAGES V05: API 650 / ASCE-7
Seismic use group | bar: TABULATION OF REVISED PAGES V05
| Importance factor | TABULATION OF REVISED PAGES V05: 1.25
| Ss | TABULATION OF REVISED PAGES V05: 1.125
| S1 | TABULATION OF REVISED PAGES V05: 0.46
Fa | bar: TABULATION OF REVISED PAGES V05
| Fv | TABULATION OF REVISED PAGES V05: 1.33
Related documents
| Document Title | [9 empty] | Document Number
| ROOF STRUCTURE CALCULATION FOR FIRE WATER TANKS (TK-2301 A/B) | [9 empty] | BK-GCS-IDR-120-ST-CN-0002
| VENT CALCULATION FOR FIRE WATER TANKS (TK-2301 A/B) | [9 empty] | BK-GCS-IDR-120-NO-CN-0005
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  | TABULATION OF REVISED PAGES V03: پروژه; TABULATION OF REVISED PAGES V04: بسته کاری; TABULATION OF REVISED PAGES V06: صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 5 | شماره صفحه:
053-073 -9184 |  | TABULATION OF REVISED PAGES V03: BK; TABULATION OF REVISED PAGES V04: GCS; TABULATION OF REVISED PAGES V06: IDR | 120 |  | ME | CN |  | 0003 | V00
Material of Parts:
| ITEM | TABULATION OF REVISED PAGES V04: Material |  | ITEM |  |  |  |  | Material
| Shell | TABULATION OF REVISED PAGES V04: A-283 GR.C |  | Wind girder/Top angle |  |  |  |  | A36 or st37-2
| Roof(Floating/Fix) | TABULATION OF REVISED PAGES V04: A-283 GR.C |  | Top Angle |  |  |  |  | A36 or st37-2
| Annular plate/Bottom plate | TABULATION OF REVISED PAGES V04: A-283 GR.C |  | Anchor Bolt |  |  |  |  | F1554 Gr.36
| Rafter | TABULATION OF REVISED PAGES V04: SA 36 |  | Anchor chair |  |  |  |  | SA516Gr70
| Manhole plate | TABULATION OF REVISED PAGES V04: A-283 GR.C |  | Internal pipes/Fitting |  |  |  |  | SA106B/A-234 Gr.WPB
| Nozzle neck pipe | TABULATION OF REVISED PAGES V04: A-106 GR.B |  | Int., bolt/nut |  |  |  |  | SA193B7/194 H- Galv.
| Nozzle neck plate | TABULATION OF REVISED PAGES V04: A-283 GR.C |  | Ext. bolt/nut |  |  |  |  | SA193B7/194 H
| Pipe Flanges/Blind | TABULATION OF REVISED PAGES V04: A-105/A-106 GR.B |  | Ladder/Stair/supports |  |  |  |  | A36 or st37-2
| Reinforcement Pad | TABULATION OF REVISED PAGES V04: A-283 GR.C |  | Gasket |  |  |  |  | Non asbestos
| Sump plate | TABULATION OF REVISED PAGES V04: A-283 GR.C
Shell plate:
| Course No. | TABULATION OF REVISED PAGES V03: Material; TABULATION OF REVISED PAGES V07: Yield Stress(Mpa) |  |  |  | Design Stress(Mpa) |  |  |  | Test Stress(Mpa)
| #1 | TABULATION OF REVISED PAGES V03: A-283 GR.C; TABULATION OF REVISED PAGES V07: 205 |  |  |  | 137 |  |  |  | 154
| #2 | TABULATION OF REVISED PAGES V03: A-283 GR.C; TABULATION OF REVISED PAGES V07: 205 |  |  |  | 137 |  |  |  | 154
| #3 | TABULATION OF REVISED PAGES V03: A-283 GR.C; TABULATION OF REVISED PAGES V07: 205 |  |  |  | 137 |  |  |  | 154
| #4 | TABULATION OF REVISED PAGES V03: A-283 GR.C; TABULATION OF REVISED PAGES V07: 205 |  |  |  | 137 |  |  |  | 154
| #5 | TABULATION OF REVISED PAGES V03: A-283 GR.C; TABULATION OF REVISED PAGES V07: 205 |  |  |  | 137 |  |  |  | 154
| #6 | TABULATION OF REVISED PAGES V03: A-283 GR.C; TABULATION OF REVISED PAGES V07: 205 |  |  |  | 137 |  |  |  | 154

## Shell Plate Design
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 6 | شماره صفحه:
053-073 -9184 |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Shell Plate Design:
Based on API 650, Shell plates shall be designed for 2 filling condition. One for product and another for hydrostatic test.
| Calculation method: One-foot method |  |  |  |  | D |  | 13 |  | m | [8 empty] | 17 | 1733
[6 empty] | G |  | 1 | [10 empty] | 7 | 713.5882
[6 empty] | Sd |  | 137 |  | mpa
[6 empty] | St |  | 154 |  | mpa
[6 empty] | CA |  | 1.6 |  | mm
Min. thickness based on tank diameter is 5 mm. (API 650- 5.6.1.1)
1000
[20 empty] | 5500 | 1500
1500
| Course | Course width (mm) |  | Liq. Height for course (m) |  |  | Design thk. (td) (mm) |  |  | Test thk. (tt) (mm) |  | D.L.H.Sthk. (tt) (mm) |  | Selected thk. (mm) |  | Course weight (Kg) |  |  |  |  | 1500
| #1 | 2000 |  | 9.5 |  |  | 5.8777 |  |  | 3.8055 |  | 8 |  | 8 |  | 5129.5925
| #2 | 2000 |  | 7.5 |  |  | 4.9477 |  |  | 2.9782 |  | 8 |  | 8 |  | 5129.5925
| #3 | 1500 |  | 5.5 |  |  | 4.0178 |  |  | 2.1509 |  | 6 |  | 6 |  | 2885.3958
| #4 | 1500 |  | 4 |  |  | 3.3204 |  |  | 1.5305 |  | 6 |  | 6 |  | 2885.3958
| #5 | 1500 |  | 2.5 |  |  | 2.6229 |  |  | 0.91 |  | 6 |  | 6 |  | 2885.3958
| #6 | 1000 |  | 1 |  |  | 1.9255 |  |  | 0.28955 |  | 6 |  | 6 |  | 1923.5972
| SUM | [14 empty] | 20838.9695
*Dynamic Liquid Hoop Stress
[9 empty] | Total weight (Kg)-Corroded condition: | [6 empty] | 18755.0725
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 7 | شماره صفحه:
053-073 -9184 |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Requirement for Impact Testing
| Course | X(mm) | Thk. Range |  | Material |  | Material Group |  | Y(°C) |  |  |  | Required M.D.M.T. (°C) |  |  | Requirement for Impact Testing
| #1 | 8 | 6≤X<13 |  | A-283 GR.C |  | I |  | -10.574 |  |  |  | 5 |  |  | Not Requirement
| #2 | 8 | 6≤X<14 |  | A-283 GR.C |  | I |  | -10.574 |  |  |  | 5 |  |  | Not Requirement
| #3 | 6 | 6≤X<15 |  | A-283 GR.C |  | I |  | -10.574 |  |  |  | 5 |  |  | Not Requirement
| #4 | 6 | 6≤X<16 |  | A-283 GR.C |  | I |  | -12.002 |  |  |  | 5 |  |  | Not Requirement
| #5 | 6 | 6≤X<17 |  | A-283 GR.C |  | I |  | -12.002 |  |  |  | 5 |  |  | Not Requirement
| #6 | 6 | 6≤X<18 |  | A-283 GR.C |  | I |  | -12.002 |  |  |  | 5 |  |  | Not Requirement

## Bottom & Annular plate design
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 8 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Bottom plate design:
The Slope of bottom is 1:120
| Corrosion allowance: |  |  |  | 1.6 | mm
| The min required thickness for carbon steel is: | [6 empty] | 6 | + | 1.6 | = | 7.6 | mm
Selected
| The selected thickness is |  |  |  | 8 | mm | à | Outside Diameter of Bottom Plate: | [5 empty] | 13066.8 |  | mm | → | 13100 |  | mm
Annular plate design:
Based on API 650, considering annular plate is not required. Also based on Bob long, the recommended diameter for considering annular plate is 12.5 m. But for proper shell settlement and good stability of tank, the annular plate will be considered.
Min. required thickness: (API 650, table 5.1.a)
[10 empty] | td |  | CA |  | Ct |  | tt |  | nt
[10 empty] | 5.8777 |  | 1.6 |  | 6.4 |  | 3.8055 |  | 8
| Product stress= |  |  |  | 91.5687 | [7 empty] | Mpa
| Hydrostatic test stress= |  |  |  |  | 73.255 | [6 empty] | Mpa
Stress in first shell course is greater of product and hydrostatic stress. So 61 is used for above table.
| First shell course: |  |  |  | 8 |  | mm
| Annular plate thickness From table: | [5 empty] | 6 | + | 1.6 | = | 7.6 | mm
| Selected annular thickness: |  |  |  | 8 | mm
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 9 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Min. required annular plate width:
Min. Width= Max. (L, 600 mm) + tc1+ 50mm
| tcl= | 8 | mm
[8 empty] | Fy= | 205 | Mpa
[8 empty] | tb= | 8 | mm
[8 empty] | G= | 1
[8 empty] | H= | 9.5 | m
[8 empty] | γ= | 0.00981
| L= | 530.6224 | mm
| Max,(L,600)= |  | 600 | mm
| Min. Width of annular = |  |  |  | 600 | + | 8 | + | 50 | = | 658 | mm
| Bottom plate weight (including annular) | [14 empty] | 11346.8189 |  |  | kg
[5 empty] | Total weight (Kg)-Corroded condition: | [10 empty] | 10212.137 |  |  | kg

## Roof design
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 10 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS | IDR | 120 |  | ME | CN |  | 0003 | V00
Fix Roof design:
| Type Roof: |  | Cone Roof Suported by Rafter
5.10.1.a:
A supported cone roof is a roof formed to approximately the surface of a right cone that is supported principally either by rafters on girders and columns or by rafters on trusses with or without columns.
5.10.2.2
Roof Plate Thickness: Roof plates shall have a nominal thickness of not less than 5 mm (3/16 in.) or 7-gauge sheet. Increased thickness may be required for supported cone roofs (see 5.10.4.4). Any required corrosion allowance for the plates of self-supporting roofs shall be added to the calculated thickness unless otherwise specified by the Purchaser. Any corrosion allowance for the plates of supported roofs shall be added to the greater of the calculated thickness or the minimum thickness or [5 mm (3/16 in.) or 7-gauge sheet]. For frangible roof tanks, where a corrosion allowance is specified, the design must have frangible characteristics in the nominal (uncorroded) condition.
| θ | = Angle of the elements to the horizontal , (Roof Slope) : | [7 empty] | 1 |  |  |  | 5.7 | (Degree)
| D | = Inside Tank Diameter | [6 empty] | 10 |  |  |  |  | 13 | m
| th | = Nominal Calculated Thickness of Roof plates = | [5 empty] | 5 | + | 1.6 | = | 6.6 | à | 8 | mm
| Wrp | = Weight of Roof Plates | [11 empty] | 10397.0888 | Kg
| Wrcp | = Corroded Weight of Roof Plates | [11 empty] | 7797.8166 | Kg
| Wraf | = Weight of Rafters & other structure | [11 empty] | 12000 | Kg
| Tw | =Total Weight (UnCorroded) | [11 empty] | 22397.0888 | Kg
| Roof appurtenances center of graviti= | [12 empty] | 0.37746 | m
Note:Calculations related to behaviors will be provided in a separate file format with SAP software. Roof Structure Calculation Book For Fire Water Storage Tank (TK-2301A/B)
| Roof plate weight : |  |  | 10397.0888 | kg |  |  |  | r= |  |  | 6.5 | m
| Structure weight* : |  |  | 12000 |  |  |  |  | l= |  |  | 6.565 | m
| Insulation Weight: |  |  | 0 |  |  |  |  | Roof Plate Thk.= |  |  | 8 | mm
| Total weight : |  |  | 22397.0888 |  |  |  |  | Insulation Thk.= |  |  | 0 | mm
* will be finalized next revision.

## roof design(2) (hidden)
#REF!
Document Title: Mechanical Calculation
#REF! |  |  |  |  | #REF! | [7 empty] | Page: 09of 30
ROOF DESIGN:
THE ROOF IS CONSIDERED SUPPORTED CONE ROOF AS DESCRIBED IN PARA 5-10-1 & 5-10-4.FOR STRUCTURE,INTERNAL RAFTERS WITH OUT COLUMN IS CONSIDERED.THEN TOP ANGLE SIZING AND RAFTERS ARE SPECIFIED IN SEC. 9. MINIMUM SIZE OF ROOF PLATE & TOP ANGLE IS AS FOLLOW:
| ROOF PLATE THICKNESS : | [6 empty] | 5+C.A. mm, MIN. OF CODE PER PARA 5-10-2-2
MIN TOP ANGLE SIZING PER PARA.5-1-5-9-e :50x50x5→Selected 80x80x8
RESULT:
| ROOF PLATE THICKNESS : | [5 empty] | 5+1mm= |  | 6 |  | mm
| ROOF SLOPE : | [7 empty] | 6 |  | degree
| ROOF WEIGHT = | [5 empty] | 6348.0534 |  |  |  | Kg
| Tank Inside Diameter | [5 empty] | 17 |  | M
| ROOF WEIGHT+ 0.03 = | [5 empty] | 6538.495 |  | Kg
NOTE:
TOP ANGLE SIZE SHALL BE CHECKED FOR INTERNAL PRESSURE, TOO. SEE SECTION 9.
| ROOF WEIGHT CORRODED = | [5 empty] | 8908.705 |  |  | Kg
| ROOF Structure WEIGHT = | [5 empty] | 5884.6455 |  |  | Kg
| Roof&attach weight= | [5 empty] | 14423.1405 |  |  | Kg
|  | attachments |  |  |  |  | 1000 |  |  | Kg
|  | snow load |  |  |  |  | 1000 |  |  | kg
#REF!
Document Title: Mechanical Calculation
#REF! |  |  |  |  | #REF! | [7 empty] | Page:10of 30
COLUMN DESIGN:
Material |  |  | SA106B | [8 empty] | 626.8695
Column Spesification: |  | OD |  | IN |  | 12"
|  |  |  | MM |  | 323.8
|  | THK |  | MM |  | 10.31 | [5 empty] | 2.3546
|  |  |  | SCH |  | 40
2460
[6 empty] | 1476 | if:
|  |  |  | MM |  | 26211.61
|  |  |  | MM |  | 22979.5281
|  | JERASION |  | MM |  | 110.8954
|  | AREA |  | MM2 |  | 10153.8848 |  |  | 549.7645
|  | Number Column |  |  |  | 1
33493.4748
2024794.2
OK.
|  | Length(cm) |  |  |  | 990
Ratio
Coefficients |  | K |  |  |  | 2
0.43063
|  | Roof&attach weight= |  |  |  | 14423.1405
𝐹_𝑦 (𝑘𝑔⁄〖𝑐𝑚〗^2 )
𝐹_𝑎𝑙𝑙 (𝑘𝑔⁄〖𝑐𝑚〗^2 )
𝑅_1
𝑅_2
𝐸(𝑘𝑔⁄〖𝑐𝑚〗^2 )
𝐹_𝑒=(𝜋^2 𝐸)⁄〖(𝐾𝐿⁄𝑅)〗^2
𝐹_𝑎𝑙𝑙⁄𝐹_𝑒
(𝐹_𝑎𝑙𝑙⁄𝐹_𝑒 ) ≤2.25
→
𝐹_𝑐𝑟=(〖0.658〗^(𝐹_𝑎𝑙𝑙/𝐹_𝑒 ) )∗(𝐹_𝑎𝑙𝑙)
(𝐹_𝑎𝑙𝑙⁄𝐹_𝑒 )" ">2.25
→
𝐹_𝑐𝑟=0.877∗𝐹_𝑒
𝐹_𝑐𝑟
𝜑𝑃_𝑛=0.6𝐹_𝑐𝑟 𝐴

## Top Angle (hidden)
National Iranian Copper Industries Company Kerman Acid Projects Effluent Treatment Plants
Project Title
Contract No:2000173 |  | Document Number: |  |  | Rev: | Date:
Class: |  | Document Title: |  |  |  | Page X of Y
Top Angle:
Min. Required top angle is 50x50x5 (API 650, 5.1.5.9 (e)).
Selected top angle: L 50x50x5 Top angle weight per meter = 5.59 Tank surrounding = 3.1415 * 3= 9.4245(m) Total weight of top angle= 9.4245*5.59= 52.7Kg Top angle section area =7.12 cm2
National Iranian Copper Industries Company Kerman Acid Projects Effluent Treatment Plants
Project Title
Contract No:2000173 |  | Document Number: |  |  | Rev: | Date:
Class: |  | Document Title: |  |  |  | Page X of Y
Top Wind girder:
Section modulus of top wind girder: (API650, 5.9.6.1) V= 165 km/hr H= 4m D= 3 m Z= (3*3*4/17) * (165/190)^2= 37.5 cm3
1.597
From table 5.20a of API 650, L 100x75x7 is selected. With this selection, the section modulus is 60.59.
This is the minimum of section modulus, but top wind girder will be extended for walkway using
Intermediate wind girder:
H1: unstiffened shell height
Wind girder design will be done in corroded condition. So, tu (uniform) = 5 -1.5 = 3.5 mm H1= 9.47 * 3.5 * (3.5/9.7)^1.5 * (190/160)^2 = 10.1 m
Transformed tank shell:
Poldokhtar Mini Refinery Project
Rev:04 |  | Document Title: Mechanical Calculation for Tank Body |  |  |  | Page: 14of 33
Document No.:POL-IPS-PMO-P1-D-ME-DRW TK0203/TK0204/TK0207/TK0208-303
| Course | W | t actual cor . | tu cor. |  | Wtr
| 1 | 1500 | 4.5 | 3.5 |  | 1700.8401
| 2 | 1500 | 3.5 | 3.5 |  | 1500
| 3 | 1500 | 3.5 | 3.5 |  | 1500
| 4 | 1500 | 3.5 | 3.5 |  | 1500
| 5 | 1500 | 3.5 | 3.5 |  | 1500
| ∑Wtr |  |  |  |  | 7700.8401
∑Wtr < H1 , So intermediate wind girder is not required.

## Top Angle & Intermediate wind g
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | 28 | از | 11 | شماره صفحه:
053-073 -9184 |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN | 0003 | V00
Top Angle:
Min. Required top angle is 80x80x80 (API 650, 5.1.5.9 (e)).
| Selected top angle: |  |  |  | L 80x80x8
| Top angle weight per meter: |  |  |  | 9.63 |  | Kg/m
| Tank surrounding |  |  |  | 40.8407 |  | m
| Total weight of top angle |  |  |  | 393.296 |  | Kg
| Top angle section area |  |  |  | 1230 |  | mm2
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | 28 | از | 12 | شماره صفحه:
053-073 -9184 |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN | 0003 | V00
Intermediate wind girder:
| H1: unstiffened shell height | [5 empty] | t(mm) |  | 6
[7 empty] | D(m) |  | 13
[7 empty] | V(km/h) |  | 232
[7 empty] | Pwd(kPa)= |  | 2.4466
[7 empty] | Pwv (kPa)= |  | 2.2066
[7 empty] | H1(mm)= |  | 12524.8449
| Course |  | W(mm) |  |  |  | t actual cor .(mm) |  |  |  | tu cor.(mm) |  |  | Wtr(mm)
| #1 |  | 2000 |  |  |  | 6.4 |  |  |  | 4.4 |  |  | 783.8117
| #2 |  | 2000 |  |  |  | 6.4 |  |  |  | 4.4 |  |  | 783.8117
| #3 |  | 1500 |  |  |  | 4.4 |  |  |  | 4.4 |  |  | 1500
| #4 |  | 1500 |  |  |  | 4.4 |  |  |  | 4.4 |  |  | 1500
| #5 |  | 1500 |  |  |  | 4.4 |  |  |  | 4.4 |  |  | 1500
| #6 |  | 1000 |  |  |  | 4.4 |  |  |  | 4.4 |  |  | 1000
| ∑Wtr | [12 empty] | 7067.6234
According to API650 3.9.7.3
If the height of the transformed shell is greater than the maximum height H1, an intermediate wind girder is required.
So intermediate wind girder is not required.
Note:Due to the protection of courses above 5 m of the tank during erection against the wind, it is recommended to use a girder connection.
|  | Wind Girder Section: | L80x80x8 |  |  | Location: |  | 3533.8117 | ±10%

## Wind overturning stability
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 13 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Wind overturning stability:
Wind load has two major effects on the tank. One is lead to buckling of tank which will be restricted by wind girder and another may lead to tank overturning.
Unanchored tank shall satisfy all of the following uplift criteria. If following criterial will not satisfy, tank shall be anchored.
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 14 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS | IDR |  | 120 |  | ME | CN |  | 0003 | V00
| WIND PRESSURE ON TANK SHELL , | [11 empty] | Pw1 = | 0.89(V/190)^2 = |  |  |  | 1.2822 | N/M2
| WIND PRESSURE ON TANK ROOF , | [11 empty] | Pw2 = | 1.48(V/190)^2 = |  |  |  | 2.147 | N/M2
|  | WIND FORCE ON TANK SHELL ,(on ver.projected areas of cyl.surfaces) | [10 empty] | Fw1= | Pw1* (ID*H) = |  |  |  | 1754.6357 | N
|  | WIND FORCE ON TANK ROOF(on hor.projected areas of con.surfaces) | [10 empty] | Fw2= | Pw2* (ΠD²/4) = |  |  |  | 284975.7111 | N
|  | V |  | H |  | ID | [6 empty] | M1= | 8334.5197 |  |  |  | N.m
|  | 232 |  | 9.5 |  | 13 | 0 |  | 0.4 |  |  |  | M2= | 1852342.1218 |  |  |  | N.m
|  | KM/H |  | M |  | M | N.m | [6 empty] | 1860676.6415 |  |  |  | N.m
|  |  | wl = 59*(8-1.5)*(203.2*7.5)^0.5= |  |  |  |  | 17735.994 |  | N/M |  |  | Fshear= | 286730.3468 |  |  |  | N
|  |  | wl=140.8*H*D= |  |  |  |  | 17388.8 |  | N/M |  |  | Mdl= | shell weight *(ID/2) |  |  |  | 1327442.3552 | N.m
|  |  | Selected= |  |  |  |  | 17388.8 |  | N/M |  |  | Mdlr= | Roof&attach weight *(ID/2) |  |  |  | 1426694.5554 | N.m
|  |  | MF= wl * (πD) * (D/2) = |  |  |  |  | 4616110.4753 |  | N/M
Checking for satisfying the above 3 equilibrium:
[8 empty] | → |  |  | 1116405.9849 |  |  | < | 2311656.1255 |  |  | PASS
[8 empty] | → |  |  | 1860676.6415 |  |  | < | 4398470.9706 |  |  | PASS
[8 empty] | → |  |  | 8334.5197 |  |  | < | 2311656.1255 |  |  | PASS
5.11.2.2 Unanchored tanks with supported cone roofs meeting the requirements of 5.10.4 shall satisfy the following criteria:
[7 empty] | → |  | 8334.5197 |  |  |  | < | 2311656.1255 |  |  |  | PASS
𝑀_𝑤=
𝑊_𝑙
𝑀_𝑃𝑖
𝐹_𝑃

## Seismic design (hidden)
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  |  | #REF! | [10 empty] | Page: 15of 30
Seismic design:
In this section the effect on seismic load will be analysis on the tank body based on Annex E of API 650. Seismic use group (SUG) = 2 Site ground motion method : Mapped ASCE-7 method Site Class: D S0 = 0.45 S1 = 0.6 SS = 1.1625 Fa (from table E.1) = 1.035
Fv (from table E.2) = 1.5
Q = 0.67 SDS = Q. Fa. SS = 0.67 * 1.035 * 1.1625 = 0.8 Av = 0.47 * SDS = 0.376 Ge = G (1-0.4 Av) = 0.8*(1- (0.4*0.376)) = 0.68 K = 1.5 T0 = 0.2 Fv.S1/Fa.SS = 0.2 ((1.5*0.6)/(1.035*1.1625))= 0.15 Ts = Fv.S1/Fa.SS = 0.75
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  |  | #REF! | [10 empty] | Page: 16of 30
|  |  | #REF! | [9 empty] | #REF!
→
#REF!
Rwi = 3.5 (for self-anchored tank from table E.4) Rwc = 2
I = 1.25 for SUG 2 (from table E.5)
Ai = 2.5*0.67*1.035*0.45*(1.25/3.5) = 0.28
Min Ai for S1>=0.6 = 0.625 * 0.45 * (1.25/3.5) = 0.1 So calculated Ai=0.28> 0.1, it is ok. TL= 4 sec For Tc < TL:
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  |  | #REF! | [10 empty] | Page: 17of 30
Ac= 2.5*1.5*0.67*1.035*0.45*(0.75/3.05)*(1.25/2)=0.2 < Ai=0.28
| D/H= | 1.3684 |  | > | 1.333
Wp = (3.1415*8.6^2/4)*9.6*1010 =563205.2 Kg Wi = (1-0.218(.82))Wp=462643.571 Kg
[8 empty] | 1727992.395 | [8 empty] | N
→
Calculation of seismic shear load:
[14 empty] | 205055.4596 | N
[14 empty] | 161603.7025 | N
[14 empty] | 111652.6977 | N
[14 empty] | 4552412.7386 | N
[14 empty] | 12531892.5775 | N
|  | 1408602.8876 |  |  |  |  | N | [6 empty] | V= | 3668108.131 | N
|  | 3386865.0942 |  |  |  |  | N
[16 empty] | 4.6278 | m
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  |  | #REF! | [10 empty] | Page: 18of 30
[9 empty] | 6.4115 | [5 empty] | m
→
[8 empty] | 7.3408 |  | 7.2724 |  |  | 2.6819
[7 empty] | → |  | 5.53 |  |  |  |  | m
[7 empty] | → |  | 6.8679 |  |  |  |  | m
[7 empty] | no.c | thk(mm) | w(mm) |  | Xi(mm) |  | Ai(mm2) |  | Ai*Xi(mm3)
[7 empty] | 1 | 8 | 1500 |  | 750 |  | 12000 |  | 9000000
[7 empty] | 2 | 6 | 1500 |  | 2250 |  | 9000 |  | 20250000
| Xs= | 4.8269 |  |  |  | m | 3 | 5 | 1500 |  | 3750 |  | 7500 |  | 28125000
[7 empty] | 4 | 5 | 1500 |  | 5250 |  | 7500 |  | 39375000
[7 empty] | 5 | 5 | 1500 |  | 6750 |  | 7500 |  | 50625000
| Xr= | #REF! |  |  | m |  | 6 | 5 | 1500 |  | 8250 |  | 7500 |  | 61875000
[7 empty] | 7 | 5 | 1500 |  | 9750 |  | 7500 |  | 73125000
[7 empty] | sum | [5 empty] | 58500 |  | 282375000
Seismic overturning moments
[12 empty] | WiXi= |  | 21067655.6719 | N.M
Ring wall Seismic moment:
[12 empty] | WsXs= |  | 989786.9299 | N.M
[12 empty] | WrXr= |  | #REF! | N.M
|  | #REF! | [6 empty] | N.M |  |  | WcXc= |  | 11079049.5879 | N.M
[12 empty] | WiXis= |  | 25174842.4447 | N.M
[12 empty] | WsXcs= |  | 1408302.5182 | N.M
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  |  | #REF! | [10 empty] | Page: 19of 30
Slab Seismic moment:
|  | #REF! | [9 empty] | N.M
tanh⁡((3.68 𝐻)/𝐷)=
𝑊_𝑠
𝑊_𝑟
𝑊_𝑓
𝑊_𝑖
𝑉_𝑖=
𝑉_(𝑐=)
→
𝑋_𝑖=
𝑋_𝑐=
cosh⁡((3.67 𝐻)/𝐷)
sinh()
sinh((3.67 𝐻)/𝐷)
(3.67 𝐻)/𝐷
𝑋_𝑖𝑠=
𝑋_𝑐𝑠=
𝑀_𝑟𝑤=
𝑀_𝑠=
𝑊_𝑝

## Seismic design2007
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 15 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Seismic Design (APP."E")
Spectral Acceleration Coefficients
Seismic Factors & Parameters(Note1)
| Site Class | [14 empty] | D
| I : Importance factor Coeff. Set by seismic use group | [14 empty] | 1.25
| Rwi : Force reduction factor for the Impulsive mode using Allow stress design method; Table E-4 | [14 empty] | 4
| Rwc : Force reduction factor for the Convective mode using Allow stress design method; Table E-4 | [14 empty] | 2
| Z : Zone Factor | [14 empty] | 0.3
| TL : Regional-Depend Transition Period, Para. E.4.6.1 | [14 empty] | 4 |  | S
| TS : FVS1/FaSS | [14 empty] | 0.54382 |  | S
| FV : Velocity Based on Site Coefficient,(as 1s Period) Table E-2 | [14 empty] | 1.33
| Fa : Acceleration based site coefficient, (at 0.2s Period)Table E-1 | [14 empty] | 1
| KS = 0.578 / ( Tanh (3.68 H / D) )^0.5 ; (Equ. E-4.5.2-c) | [14 empty] | 0.58272
| TC : First sloshing wave period =1.8Ks ( D )^ 0.5 (Equ. E-4.5.2-a) | [14 empty] | 3.7818 |  | S
| K : Coefficient to adjust spectral acceleration fr | [14 empty] | 1.5
| Q :Scaling Factor | [14 empty] | 0.67
| Sp: Design Level Peak Ground Acceleration Parameter for Sites not addressed by ASCE Method | [14 empty] | 0.33 |  | g
| S0 : Spectral response acceleration parameter at zero second=Sp | [14 empty] | 0.33 |  | g
| S1 : Spectral response acceleration parameter at one second=1.25xSp | [14 empty] | 0.46
| Ss : Spectral response acceleration parameter at short period=2.5xSp | [14 empty] | 1.125
| SDS : Design Spectral response acceleration parameter at short period (2.5*Q*Fa*S0) | [14 empty] | 0.55275
| SD1 : Design Spectral response acceleration parameter at short period | [14 empty] | 0.47
| D : Tank Inside Diameter | [14 empty] | 13 |  | m
| H:Maximum Design Product Level | [14 empty] | 8.5 |  | m
| G : Liquid Specific Gravity | [14 empty] | 1
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 16 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Ai :Impulsive Design Response Spectrum Acceleration Coefficient ; per Equ. E.4.6.1-1:
Ai = SDS ( I / Rwi ) = 2.5 Q Fa So ( I / Rwi ) => .007
Ac:Convective Design Response Spectrum Acceleration Coefficient ; per Equ. E.4.6.1-4 & E.4.6.1-5:
If Tc ≤ TL: Ac =K SD1 ( 1 / TC )( I / Rwc ) ≤ Ai
If Tc > TL : Ac =K SDI ( TL / Tc ² )( I / Rwc ) ≤ Ai
Tc ≤ TL.
Av: Vertical earthquake acceleration coefficient. ; Para. E.6.1.3 :Av = 0.47 SDS
RESULT
|  |  | Ai= |  | 0.17273 | [9 empty] | ≥ | 0.007
Tc ≤ TL |  |  | Ac= |  | 0.11651 | [9 empty] | ≤ | Ai |  | YES
Tc > TL |  |  | Ac= |  | 0.12323 | [9 empty] | ≤ | Ai |  | NO
|  |  | Av= |  | 0.25795
Dynamic Liquid Hoop Stress, Para. E.6.1.4
Ni: Impulsive hoop membrane force in tank shell, N/mm Nc: Convective hoop membrane force in tank shell, N/mm Nh: Product hydrostatic membrane force, N/mm Y: distance from liquid surface to analysis point
| Course |  | D/H |  |  |  | Y
| #1 |  | 1.5294 |  |  |  | 8.5
| #2 |  | 2 |  |  |  | 6.5
| #3 |  | 2.8889 |  |  |  | 4.5
| #4 |  | 4.3333 |  |  |  | 3
| #5 |  | 8.6667 |  |  |  | 1.5
| #6 |  | 26 |  |  |  | 0.5
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 17 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
| Course No |  | Width |  | tcr | Y | Ni |  | Nc |  | Nh |  | sigma1 (Mpa) |  |  | sigma2 (Mpa) |  |  | Ratio(E.6.2.4/σT)
| #1 |  | 2 |  | 6.4 | 8.5 | 70.238 |  | 6.8916 |  | 522.34 |  | 95.4907 |  |  | 67.7405 |  |  | 0.52407 |  | OK
| #2 |  | 2 |  | 6.4 | 6.5 | 66.3494 |  | 8.0258 |  | 394.94 |  | 73.9401 |  |  | 49.4787 |  |  | 0.4058 |  | OK
| #3 |  | 1.5 |  | 4.4 | 4.5 | 54.6836 |  | 11.8021 |  | 267.54 |  | 74.9824 |  |  | 46.6266 |  |  | 0.41152 |  | OK
| #4 |  | 1.5 |  | 4.4 | 3 | 40.8304 |  | 17.0738 |  | 171.99 |  | 49.9254 |  |  | 28.2519 |  |  | 0.274 |  | OK
| #5 |  | 1.5 |  | 4.4 | 1.5 | 22.6025 |  | 25.4703 |  | 76.44 |  | 25.3169 |  |  | 9.4285 |  |  | 0.13894 |  | OK
| #6 |  | 1 |  | 4.4 | 0.5 | 8.0203 |  | 33.5319 |  | 12.74 |  | 10.737 |  |  | -4.9461 |  |  | 0.058926 |  | OK
| MAX, σT = | [11 empty] | 95.4907
| E.6.2.4: The max. allowable hoop tension membrane stress = Min. ( 1.33 Sd , 0.9 Fy * E ) = | [15 empty] | 182.21
| E : Weld J.E. = |  |  |  | 1
| Fy= | 205 |  | Mpa |  | min=( |  | 182.21 | 184.5 | )
| Sd= | 137 |  | Mpa
| Total Combined Hoop Stress in Shell < Max. Allow. Hoop Stress | [14 empty] | OK
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 18 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Effective Weight of Product-Para E.6.1.1
WS : TOTAL WEIGHT OF TANK SHELL AND APPURTENANCES (+10% for accessories) | [16 empty] | 224644.0909 |  | N
Wr :TOTAL WEIGHT OF FIXED TANK ROOF INCLUDING FRAMING, | [16 empty] | 219491.4701 |  | N
Wf : WEIGHT OF THE TANK BOTTOM | [16 empty] | 111198.825 |  | N
Wp : TOTAL WEIGHT OF TANK CONTENT BASED ON PRODUCT SPECIFIC GRAVITY | [16 empty] | 11146528.9325 |  | N
Wi : EFFECTIVE IMPULSIVE WEIGHT OF THE LIQUID | [10 empty] | E.6.1.1-1
| E.6.1.1-1 | [5 empty] | Yes |  |  | E.6.1.1-2 | [6 empty] | No
| Wi= | 7304032.7942 |  |  |  |  | N |  |  | Wi= | 7430145.0508 | [5 empty] | N
WC : EFFECTIVE CONVECTIVE (SLOSHING) PORTION OF THE LIQUID WEIGHT, Equ. E-6.1.1-3 :
| Wc = 0.230 D/H Tanh(3.67 H / D)*Wp = | [15 empty] | 3856896.4604 |  | N
Center of Action for Effective Lateral Forces E.6.1.2
| Xr :Height from the bottom of the tank shell to the roof and roof appurtenances center of gravity | [15 empty] | 9.5 |  | m
| Xs : HEIGHT FROM BOTTOM OF THE TANK TO SHELL CENTER OF GRAVITY | [15 empty] | 4.6568 |  | m
| NO.Course |  |  | thk(mm) |  |  | W(m) |  |  | Xi(m) |  |  | Wi(kg) |  |  | Wi.Xi(Kg.m)
| #1 |  |  | 8 |  |  | 2 |  |  | 1 |  |  | 5129.5925 |  |  | 5129.5925
| #2 |  |  | 8 |  |  | 2 |  |  | 3 |  |  | 5129.5925 |  |  | 15388.7775
| #3 |  |  | 6 |  |  | 1.5 |  |  | 4.75 |  |  | 2885.3958 |  |  | 13705.6299
| #4 |  |  | 6 |  |  | 1.5 |  |  | 6.25 |  |  | 2885.3958 |  |  | 18033.7236
| #5 |  |  | 6 |  |  | 1.5 |  |  | 7.75 |  |  | 2885.3958 |  |  | 22361.8172
| #6 |  |  | 6 |  |  | 1 |  |  | 7 |  |  | 1923.5972 |  |  | 13465.1803
| Sum: | [5 empty] | 9.5 |  |  | 29.75 |  |  | 18915.3723 |  |  | 88084.7209
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 19 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
center of gravity(m) |  |  | Xs=∑(Xi.Wi)/∑Wi |  |  |  |  | 4.6568 |  | m
| Xis ::Height from the bottom of the tank shell to the center of action of the lateral seismic force related to the impulsive liquid force for slab moment | [15 empty] | E.6.1.2.2-1
When D/H is greater than or equal to 1.3333, the height Xis is determined by Equation E.6.1.2.2-1:
When D/H is less than 1.3333, the height Xis is determined by Equation E.6.1.2.2-2:
| E.6.1.2.2-1 | [6 empty] | Yes |  |  |  | E.6.1.2.2-2 |  |  |  |  | No |  |  | .
| Xis= | 5.4228 | [5 empty] | m |  |  | Xis= | 5.03 | [5 empty] | m
Xcs ::Height from the bottom of the tank shell to the center of action of the lateral seismic force related to the Convective liquid force for slab moment. E.6.1.2.2-3:
[10 empty] | 6.1546 | [7 empty] | m
Xi : Height from the bottom of the tank shell to the center of action of the lateral seismic force related to the impulsive liquid force for ringwall moment
| (E.6.1.2.1-1) | [6 empty] | Yes |  |  |  | (E.6.1.2.1-2) | [5 empty] | No
| Xi= | 3.1875 | [5 empty] | m |  |  |  | Xi= | 3.028 | [5 empty] | m
Xc : Height from the bottom of the tank shell to the center of action of the lateral seismicforce related to the convective liquid force for ringwall moment
[9 empty] | 5.5472 | [7 empty] | m
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 20 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Design Load; para E.6.1 :
| V = Total Design Base Shear : ( Vi ² + Vc²)^0.5 = | [9 empty] | 1430022.7822 |  |  |  |  | N
| Vi = Design Base shear due to impulsive force = Ai ( Ws + Wr + Wf + Wi ) = | [13 empty] | 1357582.8778 |  |  |  | N
| Vc = Design Base shear due to Convective force = Ac Wc = | [13 empty] | 449370.546 |  |  |  | N
Seismic overturning moments
Ring wall Seismic moment:
| Mrw= |  | 5198984.1277 | [13 empty] | N.M
Slab Seismic moment:
| MS= |  | 7883620.131 | [13 empty] | N.M
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 21 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Checking the self-anchored Tank, Para E.6.2.1.1:
Wa = Resisting force of tank contents per unit length of shell circumference that may be used to resist the shell overturning moment, N/m
[6 empty] | No | [13 empty] | Yes
Wa = 99 ta (Fy * Ge * H)^0.5 = | [5 empty] | 25046.9128 |  | N/M |  | à | Wa>201.1GeHD |  |  |  | à |  |  |  | = | 65656.6406
201.1Ge H D= | [7 empty] | 19928.7305
Fy:Minimum specified yield strength of bottom annulus, Mpa = | [12 empty] | 205 |  | Mpa
Ge:Effective specific gravity including vertical seismic effects=G(1 – 0.4Av)= | [14 empty] | 0.89682
ta:Thickness of the bottom plate under the shell extending at least the distance, L,from the inside of the shell,less corrosion allowance, mm | [15 empty] | 6.4 |  | mm
[10 empty] | 2.8958 |  | > | 0.785
Wt :Tank and roof weight acting at base of shell, N/m | [16 empty] | 11412.2593
Wrs: Roof load acting on the shell, including the specified snow load N/m = | [14 empty] | 5911.7643
wint: Calculated design uplift load due to product pressure per unit circumferential length, N/m | [17 empty] | 0
RESULT:
Tank is not stable and cannot be self-anchored for the design load.Modify the annular ring if L<0.0035 D is not controlling or add mechanical anchorage.
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 22 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Shell Compression in Mechanically-Anchored Tanks E.6.2.2.2
Shell Compression in Mechanically-Anchored Tanks(Para.E.6.2.2.2)
t | Thickness of Bottom Shell Course | [13 empty] | 8 |  | mm
C.A. | Corrosion Allowance of Bottom Shell Course | [13 empty] | 1.6 |  | mm
ts | Corroded Thickness of Bottom Shell Course | [13 empty] | 6.4 |  | mm
σc | Max. Shell Compression Stress at the bottom of the shell | [13 empty] | 8.0861
| No | [8 empty] | Yes
| GHD^2/t^2= |  |  | 22.4453
| 0.5Fty = |  |  | 102.5
Fc | Allowable longitudinal shell membrane compression stress in tank shell | [13 empty] | 38.2107
Fty | Minimum specified yield strength of shell course, Mpa | [13 empty] | 205 |  | Mpa
RESULT:
| Fc < 0.5Fty |  |  |  | ok
| σc < Fc |  |  |  | ok
SLIDING RESISTANCE (Para.E.7.6)
Self-anchored storage tanks shall be proportioned such that the calculated seismic base shear, V, does not exceed Vs:
| µ=Friction coefficient for tank sliding (Max. = 0.4)= | [9 empty] | 0.4
| Vs=Max. seismic base shear Force= | [6 empty] | 4197786.0245
RESULT:
Vs > V so Tank is stable against Seismic Sliding
LOCAL SHEAR TRANSFER (ParaE.7.7)
| Vmax=Peak local tangential shear per unit length | [11 empty] | = | 70029.2906 |  | N/M
| σv=Peak local tangential shear Stress = Vmax/(t‐C.A.) | [9 empty] | 10.9421 |  | Mpa
RESULT:
Since Shear Stress is Less than Shear Allowable Stress, So Local Shear Transfer is ok
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 23 | شماره صفحه:
053-073 -9184 |  |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
FREEBOARD CHECKING (Para. E.7.2):
Note: E.4.6.1 Spectral Acceleration Coefficients For tanks falling in SUG III, the mapped value of TL shall be used to determine both convective forces and sloshing wave height except that the importance factor, I, shall be set equal to 1.0 in the determination of sloshing wave height. In regions outside the USA, where the regulatory requirements for determining design ground motion differ from the ASCE 7 methods prescribed in this Annex, TL shall be taken as 4 seconds.
Height of the sloshing wave above the product design height will calculate by following equation:
δs = 0.42 D Af= |  |  |  | 0.65098 |  | m
For SUG III
[5 empty] | I : Importance factor Coeff. Set by seismic use group= | [5 empty] | 1
|  | Tc= |  |  | 3.7818 |  | à | E.4.5.2-a |  |  | Tc= 1.8Ks D0.5
| When, TC ≤ 4 |  |  |  |  | Af= | 0.11923 |  |  |  | à | Yes
| When, TC > 4 |  |  |  |  | Af= | 0.15763 |  |  |  | à | No
|  | SDS= |  | 0.55275 |  | g |  |  | 0.33 |  | g |  |  | 0.7 δs |  |  | 0.45569 |  | m
|  | HLL | = |  |  | 8.5 | m | →
|  | depth of Submersion |  |  | = | 0 | m |  |  | 1 | m → | SO FREEBOARD REQUIREMENT HAS BEEN SATISFIED
|  | Shell height |  | = |  | 9.5 | m
→
→
→
→
≥
→
→

## Anchor Bolt
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 24 | شماره صفحه:
053-073 -9184 |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Anchor Bolt Sizing
| Min. qty. of bolts = 3.1415*D/2= | [5 empty] | 15.708
| Considered qty. of bolts = | [5 empty] | 16 |  |  | Bolt Center Diameter= |  |  |  | 13200 |  | mm
|  | Outside Diameter of Bottom plate: |  |  |  |  | 13100 |  | à | Anchore Bolt will Not clash with Bottom Plate | [7 empty] | à | Pass
| Inside Diameter of Anchore Bolt: | [5 empty] | 13173
| Circumferential distance between bolts = | [7 empty] | 2.5525 |  | OK
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 25 | شماره صفحه:
053-073 -9184 |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Anchor bolt material : |  |  |  | F1554 Gr.36
Uplift Load Case |  |  |  | U(N) |  |  | tb = U/N |  |  | Sall=Allowable Anchor Bolt Stress (Mpa) |  |  | Sb=tb/Ab (Mpa) |  | Ab‐anchor Bolt Area (mm2) |  | Bolt Size (Request)
Design Pressure |  |  |  | -714930.4981 |  |  | -44683.1561 |  |  | 103.3333 |  |  | 136.6667 |  | Not Required |  | -
Test Pressure |  |  |  | -843598.0575 |  |  | -52724.8786 |  |  | 137.7778 |  |  | 170.8333 |  | Not Required |  | -
Failure Pressure |  |  |  | -444982.6399 |  |  | -27811.415 |  |  | 248 |  |  | 205 |  | Not Required |  | -
Frangibility Press. |  |  |  | -637983.9789 |  |  | -39873.9987 |  |  | 248 |  |  | 205 |  | Not Required |  | -
Wind Load |  |  |  | -666654.8237 |  |  | -41665.9265 |  |  | 198.4 |  |  | 170.8333 |  | Not Required |  | -
Seismic Load |  |  |  | 1001355.0397 |  |  | 62584.69 |  |  | 198.4 |  |  | 170.8333 |  | Required |  | 315.447
Pdesign+Wind |  |  |  | -714414.2237 |  |  | -44650.889 |  |  | 137.7778 |  |  | 170.8333 |  | Not Required |  | -
Pdesign+seismic |  |  |  | 1051422.7917 |  |  | 65713.9245 |  |  | 198.4 |  |  | 170.8333 |  | Required |  | 331.2194
required anchor bolt diameter | [16 empty] | 331.2194
Av = vertical earthquake acceleration coefficient,%g | [15 empty] | 0.25795
PWR = Wind uplift pressure on roof in (Kpa) | [15 empty] | 0.002147
PWS = wind pressure on shell in (N/m2) | [15 empty] | 1.2822
D= Tank diameter in (m) | [15 empty] | 13
H = tank height, in meters; | [15 empty] | 9.5
P= design pressure in (Kpa) | [15 empty] | 0
Pf = failure pressure in (KPa) = 1.6 P -‐((0.000746DLR)/D²)th [ACC. tO F.6.] | [15 empty] | -0.96987
DLR is the nominal weight of roof plate plus any attached structural, in N. | [15 empty] | 219715.4409
th = roof plate thickness (mm) = | [15 empty] | 8
Mw = wind moment in (N‐m) = | [15 empty] | 1860676.6415
MWH = PWS × D × H²/2 (N-m) | [15 empty] | 752.1904
Mrw = seismic moment in (N‐m) = | [15 empty] | 5198984.1277
W1 = dead load of shell minus any corrosion allowance and any dead load other than roof plate acting on the shell minus any corrosion allowance (N) = Shell(Cr.) + Shell attachements(Cr.) = | [15 empty] | 525824.3213
W2 = dead load of shell minus any corrosion allowance and any dead load including roof plate acting on the shell minus any corrosion allowance (N) = W1 + Roof(Cr.) = | [15 empty] | 667171.0981
W3 = dead load of the shell using as built thicknesses and any dead load other than roof plate acting on the shell using as built thicknesses (N). = | [15 empty] | 204221.9008
N= Number of bolt using in the calculation | [15 empty] | 16
Fy= | [15 empty] | 248
Fty= | [15 empty] | 205
According to API 650 3.12.5
The minimum anchor bolt diameter is 1" plus any specified corrosion allowance
| anchor bolt diameter= |  |  |  | M | 27 | → | 414 |  | mm2 |  | Yes
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 26 | شماره صفحه:
053-073 -9184 |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Anchor chair part calculation
Diameter of tank | [9 empty] | D= |  | 13 |  | m
Top Plate Width along shell | [9 empty] | a= |  | 300 |  | mm |  |  | 11.811 |  | Inch
Bolt Circle diameter | [9 empty] | B.C.D.= |  | 13200 |  | mm |  |  | 519.685 |  | Inch
Pad Palte Thickness | [9 empty] | t Pad= |  | 20 |  | mm |  |  | 0.7874 |  | Inch
Shell Plate thickness | [9 empty] | t shell= |  | 8 |  | mm |  |  | 0.31496 |  | Inch
Number of anchor bolts | [9 empty] | nBolt= |  | 16
Anchor bolt diameter | [9 empty] | d= |  | 27 |  | mm |  |  | 1.063 |  | Inch
Hole diameter | [9 empty] | dhole= |  | 31 |  | mm |  |  | 1.2205 |  | Inch
Anchor bolt eccentricity | [9 empty] | e= |  | 72 |  | mm |  |  | 2.8346 |  | Inch
Distance from outside of top plate to centerline of bolt(min. 1.5*hole diameter) | [9 empty] | F= |  | 90 |  | mm |  |  | 3.5433 |  | Inch
Distance from outside of top plate to edge of hole | [9 empty] | f= |  | 74.5 |  | mm |  |  | 2.9331 |  | Inch
Top Plate length in raidial direction(min 3*hole diameter) | [9 empty] | b= |  | 162 |  | mm |  |  | 6.378 |  | Inch
Distance between vertical plates | [9 empty] | g= |  | 160 |  | mm |  |  | 6.2992 |  | Inch
Chair height( minimum 6") | [9 empty] | h= |  | 360 |  | mm |  |  | 14.1732 |  | Inch
Vertical Palates(gusset) thickness | [9 empty] | j= |  | 15 |  | mm |  |  | 0.59055 |  | Inch
Gusset lowest width | [9 empty] | L Gusset= |  | 33 |  | mm |  |  | 1.2992 |  | Inch
Vertical plates width(average width for tapered plates) | [9 empty] | k= |  | 96.4 |  | mm |  |  | 3.7953 |  | Inch
Bottom plate thickness (Corroded) | [9 empty] | m= |  | 6.4 |  | mm |  |  | 0.25197 |  | Inch
Nominal Shell Radius | [9 empty] | R= |  | 6500 |  | mm |  |  | 255.9055 |  | Inch
Minimum yield stength of chair parts | [9 empty] | Sy= |  | 260 |  | Mpa |  |  | 38.0489 |  | ksi
Shell thickness(Corroded) also including the pad thickness | [9 empty] | t= |  | 26.4 |  | mm |  |  | 1.0394 |  | Inch
Ringwall moment | [9 empty] | Mrw= |  | 5198984.1277 |  | N.m
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک |  | سریال | نسخه | 28 | از | 27 | شماره صفحه:
053-073 -9184 |  |  |  | BK | GCS |  | IDR |  | 120 |  | ME | CN |  | 0003 | V00
Calculated design uplift load on anchors per unit circumferential length | [10 empty] | Wa= |  | 65713.9245 |  | N/m
Actual bolt load | [10 empty] | Pa= |  | 167737.6857 |  | N |  | 37.7074 |  | kip
Yield strenth of anchor bolt (A 36) | [10 empty] | Fy= |  | 248 |  | Mpa |  | 36.2928 |  | ksi
Deign load will be the lesser of bellow items:
1- 3 thime of PA,B | [10 empty] | P1= |  | 503213.0571 |  | Mpa |  | 113.1223 |  | kip
Cross section area of bolt*yiled strenth of Anchol bolt | [10 empty] | As= |  | 414 |  | mm2 |  | 0.6417 |  | inch2
Cross Section Area of Bolt | [10 empty] | Sd1= |  | 148.8 |  | Mpa |  | 21.576 |  | ksi
Allowance design Stress for anchor chair parts | [10 empty] | Sd2= |  | 156 |  | Mpa |  | 22.62 |  | ksi
[11 empty] | P2= |  | 102672 |  | N |  | 23.2891 |  | kip
Desing load | [10 empty] | P= |  | 102672 |  | N |  | 23.2891 |  | kip
Reduction factor= | [10 empty] | Z= |  | 0.954
Stress at point= | [10 empty] | S= |  | 16.3538 |  | ksi
[11 empty] | Sd= |  | 22.62 |  | ksi
|  |  |  | So stress is smaller than Allowance desing for anchor chair | [9 empty] | à | Ok
Minimum chair height h = 6 in (152.4 mm) , except h = 12 in (304.8 mm) when base plate or bottom plate is 3/8 in (9.525 mm)
or thinner and where earthquake or winds over 100 mph (160 km/h) must be considered.
Verification of Chair Height: | [9 empty] | h= |  | 360 |  | mm |  | à | Ok
Verification of Top Plate Thickness:
Thickness of top plate | [9 empty] | C= |  | 21.9545 |  | mm |  |  | 0.86435 |  |  | Inch
[10 empty] | C= |  | 25 |  | mm |  |  | 0.98425 |  |  | Inch
Verification of Gusset Thickness:
jmin = Max (1/2 in , 0.04 (h - c) ) | [9 empty] | j1= |  | 12.7 |  | mm |  |  | 0.5 |  |  | Inch
[10 empty] | j2= |  | 13.4 |  | mm |  |  | 0.52756 |  |  | Inch
[10 empty] | j= |  | 35 |  | mm |  |  | 1.378 |  |  | Inch
[7 empty] | Should be: |  | j > P / (25*k) |  |  | à |  | Ok
WELD SIZE CHECKING:
Load per horizontal line | [9 empty] | WH = |  | 38.0182 |  | N/mm |  |  | 0.21904 |  | kip/Inch
Load per vertical line | [9 empty] | WV = |  | 100.6588 |  | N/mm |  |  | 0.57995 |  | kip/Inch
Total load per line | [9 empty] | W= |  | 107.5992 |  | N/mm |  |  | 0.61993 |  | kip/Inch
|  |  | Should be: |  | w >= W / 9.6 |  |  |  |  | W / 9.6= |  | 11.2082 |  | mm |  |  | 0.064576 |  | Inch
[12 empty] | 10 |  | mm |  |  | 0.3937 |  | Inch

## Summary
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Fire Water Tank (TK-2301A/B)
شماره پیمان: |  | پروژه | بسته کاری |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | 28 | از | 28 | شماره صفحه:
053-073 -9184 |  | BK | GCS |  | IDR |  | 120 | ME | CN | 0003 | V00
Fabrication Data
| Item |  |  |  | Thickness(mm) |  |  | weight (Kg)
| Shell#1 |  |  |  | 8 |  |  | 5129.5925
| Shell#2 |  |  |  | 8 |  |  | 5129.5925
| Shell#3 |  |  |  | 6 |  |  | 2885.3958
| Shell#4 |  |  |  | 6 |  |  | 2885.3958
| Shell#5 |  |  |  | 6 |  |  | 2885.3958
| Shell#6 |  |  |  | 6 |  |  | 1923.5972
| Bottom plate weight (including annular) |  |  |  | 8 |  |  | 11346.8189
| Fix Roof Plate(Including Structure) |  |  |  | 8 |  |  | 22397.0888
| Top Angle |  |  |  | L 80x80x8 |  |  | 393.296
| Intermediate wind girder |  |  |  | 0 |  |  | 224.9424
| Nozzles |  |  |  | estimate |  |  | 2500
| Spiral Stair way |  |  |  | estimate |  |  | 2598
| Unseen(3% of total weight) |  |  |  | estimate |  |  | 1808.9735
| Empty |  |  |  | Weight(kg) |  |  | 62108.089
| Hydrotest | [6 empty] | 1322108.089
| Operating | [6 empty] | 1102108.089
Foundation Load Data
| Seismic |  |  | Shear(N) |  |  |  | 1430022.7822
|  |  |  | Moment (N.m) |  | Ring Wall |  | 5198984.1277
[6 empty] | Slab |  | 7883620.131
| Wind |  |  | Shear(N) |  |  |  | 286730.3468
|  |  |  | Moment (N.m) |  |  |  | 1860676.6415

## Anchorage ratio (J) (hidden)
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 20of 30
Anchorage ratio (J):
The need for anchorage due to seismic load will be checked by anchorage ration. If anchorage ratio be greater than 1.54, tanks shall be anchored.
D: Tank Diameter, m Mrw: Ring wall seismic moment, N.m Ws: total weight of tank shell and appurtenances, N wrs: roof load acting on shell including 10% of roof specified snow load, N/m Av: vertical earthquake acceleration parameter, %g Wa: force resisting uplift in annular region, N/m Wint: Calculated design uplift load due to product pressure per unit circumferential length, N/m There is now internal pressure, so wint=0.
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 21of 30
161608.7234
| Ge=G(1-0.4Av) |  |  | 0.8532
[10 empty] | 26335.1933 |  |  |  | > | 21358.831
| so,L=0.035 D |  |  | 332.5 |  |  | MM | (the assumed previous calculated annular width is ok.)
| J | 1-0.4*Av |  |  | 0.8496 |  |  | #REF!
169
0
Dynamic liquid hoop stress:
| Ni: Impulsive hoop membrane force in tank shell, N/mm Nc: Convective hoop membrane force in tank shell, N/mm Nh: Product hydrostatic membrane force, N/mm Y: distance from liquid surface to analysis point | [13 empty] | D/H= |  | 1.3684
[15 empty] | Y= |  | 8.5
[15 empty] | 0.75D= |  | 6.45
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 22of 30
| course | course width | tcr |  | y |  | Ni |  | Nc |  | Nh |  | sigma1 (Mpa) |  |  | sigma 2 (Mpa)
| 1 | 1.5 | 6.5 |  | 9.3 |  | 54.3813 |  | 0.70162 |  | 187.4439 |  | 38.2619 |  |  | 19.4132
| 2 | 1.5 | 4.5 |  | 7.8 |  | 54.3813 |  | 1.079 |  | 153.5685 |  | 47.258 |  |  | 20.9946
| 3 | 1.5 | 3.5 |  | 6.3 |  | 54.3813 |  | 1.9163 |  | 119.6931 |  | 50.5739 |  |  | 17.8222
| 4 | 1.5 | 3.5 |  | 4.8 |  | 54.3813 |  | 3.5706 |  | 85.8177 |  | 40.521 |  |  | 8.5176
| 5 | 1.5 | 3.5 |  | 3.3 |  | 54.3813 |  | 6.7471 |  | 51.9423 |  | 30.6556 |  |  | -0.9743
| 6 | 1.5 | 3.5 |  | 1.8 |  | 54.3813 |  | 12.8 |  | 18.0669 |  | 21.143 |  |  | -10.819
| 7 | 1.5 | 3.5 |  | 0.3 |  | 54.3813 |  | 24.31 |  | -15.8085 |  | 12.5162 |  |  | -21.5496
| MAX, σT = | [11 empty] | 50.5739
|  | Min(1.33Sd or 0.9FyE) | [7 empty] | MIN |  | 145.768 |  | Or | 155.448
Hoop stresses are less than material product stress and need not to check the hoop allowable. But in the following the hoop allowable stress is calculated.
Allowable hoop stress:The maximum allowable hoop tension membrane stress for the combination of hydrostatic product and dynamic membrane hoop effects shall be lesser of: - The basic allowable membrane for the shell plate material (Sd) increased by 33%; or, - 0.9Fy times the joint efficiency where Fy is the lesser of the published minimum yield strength of the shell material or weld material.
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 23of 30
Sall(hoop) = min. (1.33Sd , 0.9.Fy.E) Sd= 109.6 MPa Fy= 203.2 MPa E=0.85(for radiography based on section 8 of API 650) Sall (hoop) = min. (1.33*109.6 , 0.9*203.2*1) = min. (145.8 , 155.448) = 145.8 MPa Sall is the maximum allowable stress for dynamic hoop stress and the actual hoop stress shall be lesser than Sall. Based on above table, all hoop stresses are lesser than allowable.
Maximum longitudinal shell-membrane compression stress:
The maximum longitudinal shell compression stress at the bottom of the shell for mechanically anchored tanks shall be determined by the following formula:
#REF!
Mpa
Allowable longitudinal shell membrane compression stress in tank shell:
GHD^2/t2= 1.01*10.5*8.6*8.6/(4.5^2)= 38.74< 44 Fc= [83*4.5/(2.5*8.6)]+ 7.5*(1.01*10.5)^0.5= 41.8MPa < 0.5*205=101.6 σc<Fc, So the longitudinal compression stress is passed.
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 24of 30
Sliding resistance:
For self-anchored tank, the shear force shall be lesser than the resisting friction force between the tanks bottom and ground. It should be noted that this tank to be anchored and need mot considering sliding resistance.
µ=0.4
|  | 4421387.876 | [5 empty] | N | > |  | 3668108.131
Vs > V so Tank is stable against Seismic Sliding then self ancher is ok
Sloshing and free board:
Tc=3.25<4, So Af= 2.5*1.5*0.67*1.035*0.45*1.25*(0.75/3.25)=0.33 δs= 0.42*8.6*0.33=1.19m Based on table E.7, for SUG 2: Free board = 1.19*0.7=0.833 m
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 25of 30
Anchor bolt design:
Min. qty. of bolts = 3.1415*8.6/3=9 Considered qty. of bolts = 12 Circumferential distance between bolts = 3.1415*8.6/12= 2.25m < 3 m
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 26of 30
Anchor bolt material : SA307-B
| Pi | 0 |  |  | Mrw |  |  | #REF! |  |  | Av |  |  |  | 0.376
| Pt | 0 |  |  | Fp |  |  | 0.4 |  |  | Pws(N/M2) |  |  |  | 1282.2338
| Pf | 0 |  |  | W1 |  |  | 215308.2326 |  |  | Fy |  |  |  | 240
| Pwr | 2.147 |  |  | W2 |  |  | 302969.8895 |  |  | Fty |  |  |  | 205
| Mwh | 158355.8737 |  |  | W3 |  |  | 20838.9695
| Uplift Load Case |  |  | U(N) |  |  | tb = U/N |  |  | Sall=Allowable Anchor Bolt Stress (Mpa) |  |  | Sb=tb/Ab (Mpa) |  | Ab‐anchor Bolt Area (mm2) |  | dia
| Design Pressure |  |  | -241898.0666 |  |  | -20158.1722 |  |  | 100 |  |  | 136.6667 |  | NA |  | NA
| Test Pressure |  |  | -241898.0666 |  |  | -20158.1722 |  |  | 133.3333 |  |  | 170.8333 |  | NA |  | NA
| Failure Pressure |  |  | -47428.8035 |  |  | -3952.4003 |  |  | 240 |  |  | 205 |  | NA |  | NA
| Frangibility Press. |  |  | -47428.8035 |  |  | -3952.4003 |  |  | 240 |  |  | 240 |  | NA |  | NA
| Wind Load |  |  | -79089.9691 |  |  | -6590.8308 |  |  | 192 |  |  | 170.8333 |  | NA |  | NA
| Seismic Load |  |  | #REF! |  |  | #REF! |  |  | 192 |  |  | 170.8333 |  | #REF! |  | #REF!
| Pdesign+Wind |  |  | -18018.1462 |  |  | -1501.5122 |  |  | 133.3333 |  |  | 170.8333 |  | NA |  | NA
| Pdesign+seismic |  |  | #REF! |  |  | #REF! |  |  | 192 |  |  | 170.8333 |  | #REF! |  | #REF!
| Max | [15 empty] | #REF!
Diameter of bolt = 39.7+ 1.5= 42.7 So, selected size of anchor bolts are M44.
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 27of 28
Anchor chair design:
Anchr chair to is designed based on AISI standard. Typical anchor chair is shown below:
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 28of 30
Material of anchor chair = SA283-C Assumed dimension of top plate width along shell: (a) = 14 in. (350mm) Assumed dimension of top plate length radial direction: (2) = 12 in. Anchor bolt diameter (d) = 1 in. (26mm) Anchor bolt eccentricity (e) = 6 in. (150mm) emin = 0.886 (1.4) + 0.572 = 1.81 in. (45.5mm) Assumed distance from outside of top plate to edge of hole: (f)= 5.4 in. fmin = 0.5 (1.4) + 0.125 = 0.825in. (21mm) Assumed distance between vertical plates: (g) = 10 in. (250mm) Vertical plate average width (K) = 7 in. (175mm) Bottom or base plate thickness (m) = 0.32 in. (8mm) Nominal shell radius (R)= 388 in. (9800/2mm) First shell course thickness in corroded condition (t1) = 0.25 in. (6.5mm)
Pad thickness (t2)= 0.25 in. (6mm) Thickness in equation = 0.25+0.18 = 0.43 in (10.5mm) Actual Bolt load = 100967.39 N = 22.7 Kips Max. Allowable bolt load = 120749 N = 27.14 Kips Design load (P) = min. (1.5*22.7 , 27.14) = 34.05 Kips Stress of shell course or anchor chair plates = 20000 psi = 20 Ksi
Vertical plate thickness calculation:
C= [(27.14/(20*5.4))*(0.375*10- 0.22*1.4)]0.5= 0.93 in (=23.25 mm) Selected thickness is 25 mm = 1in. It should be noted that the radial projection of top plate shall not be more than ½ in.
Anchor chair height selection and checking: Assumed chair height = 16 in Max. Chair height for the selected dimensions = 3*a = 48 in.
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 29of 30
With 16 in chair height, the stress at the shell attachment point shall be less than the allowable stress from table which is 170.83 MPa = 24.8 Ksi
Z= 1/((0.177*14*0.32)/((0.43*388)^0.5)*((〖0.32/0.42)〗^2)+1) = 0.96
S=(27.14*6/0.43^2)((1.32*0.96)/((1.43*14*〖16〗^2)/(388*0.43) 〖+(4*14*16^2)〗^0.333 )+0.031/√(388*0.43))=22.4 Ksi < 24.8
So the chair height is ok.
Thickness of vertical plates: Jmin = max. (1/2” , 0.04(h-c)) = max. (1/2” , 0.04(16-1))=max. (0.5, 0.6)= 0.6 in. (15mm) Requirement is jK> P/25 jK= 0.6*7=4.2 P/25=27.14/25=1.08 4.2> 1.08, so the thickness of vertical plate = 15mm is ok.
Anchor chair welding size: The loads per inch of length are:
Wv=27.14/(14+2*16)=0.59 WH=(27.14*6)/(14*16+0.667*16^2)=0.41 W=(0.59^2+0.41^2)^0.5=0.72
→
Poldokhtar Mini Refinery Project
Document Title: Mechanical Calculation
#REF! |  |  | #REF! | [11 empty] | Page: 30of 30
The size of weld (w) shall be greater than W/9.6 W/9.6 = 0.72/9.6 = 0.075 in. = 1.875 mm Selected size of weld for anchor chair is 6mm.
𝑊_𝑡=
→
→
→
→
𝐷^2
→
𝑊_𝑖𝑛𝑡
→
→
→
𝐹_𝑎=
→
𝑉_𝑠=