## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | 8 | از | 1 | شماره صفحه:
| 9184 – 073 - 053 |  |  | BK |  | GCS | IDR | 120 |  | ME | CN | 0001 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209) نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | NOV.2024 |  | IFI |  |  |  | iDrill M.E. |  |  | M.Fakharian |  | M.Sadeghian
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  |  | 8 | از | 2 | شماره صفحه:
| 9184 – 073 - 053 |  |  | BK | GCS |  | IDR | 120 | ME | CN | 0001 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 | V02 |  |  | V03 |  | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 | [9 empty] | 69
10 | [9 empty] | 70
11 | [9 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## CONTENTS
NISOC |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | 8 | از | 3 | شماره صفحه:
9184 – 073 - 053 |  | BK | GCS | IDR | 120 | ME | CN | 0001 | V00
CONTENTS
Page
| 1)Introduction | [8 empty] | 4
| 2)Design Data | [8 empty] | 5
| 3)Shell Thickness | [8 empty] | 6
| 4)Bottom | [8 empty] | 7
| 5)Roof Plate | [8 empty] | 7
| 6)Tank Capacity: | [8 empty] | 7
| 7)Water Load: | [8 empty] | 8
| 8)Snow Load | [8 empty] | 8
| 9)Wind Load | [8 empty] | 8
| 10) Body Load | [8 empty] | 8

## INTRODUCTION
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | 8 | از | 4 | شماره صفحه:
9184 – 073 - 053 |  |  | BK | GCS | IDR | 120 | ME | CN | 0001 | V00
1) INTRODUCTION
Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city. With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also, PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.
GENERAL DEFINITION:
The following terms shall be used in this document. CLIENT: National Iranian South Oilfields Company (NISOC) PROJECT: Binak Oilfield Development – Manufacturing (w/Engineering & Material Supply) of Gas Dehydration Package. EPD/EPC CONTRACTOR (GC): Petro Iran Development Company (PEDCO) EPC CONTRACTOR/PURCAHSER: Joint Venture of: Hirgan Energy – Design & Inspection Companies (HE/DI) VENDOR: iDrill Middle East (iDrill M.E)
Purpose:
The purpose of this technical document is to provide the Mechanical Calculations for Elevated Potable Water Tank.

## DESIGN DATA
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  |  | 8 | از | 5 | شماره صفحه:
9184 – 073 - 053 |  |  |  | BK | GCS | IDR | 120 | ME | CN | 0001 | V00
2)DESIGN DATA
|  | DATA | [7 empty] | UNIT | Remark
GENERAL & PROCESS DATA
|  | Item | [8 empty] | TK-2209
|  | Fluid | [8 empty] | POTABLE WATER TANK
|  | Design Code | [8 empty] | API 650/AWWA D100a-11
|  | Nominal / Working Capacity | [7 empty] | m3 | 25 |  | / |  | 20
|  | Dimension | Internal Dia. | [6 empty] | mm | 3500
|  |  | Height | [6 empty] | mm | 2600
|  | Density | [7 empty] | kg/m3 | 1000
|  | Design Pressure | [7 empty] | barg | ATM + FULL OF WATER
|  | Design Temperature | [7 empty] | ºC | 85
|  | Test Pressure | [7 empty] | barg | ATM + FULL OF WATER
|  | Joint Efficiency | [7 empty] | - | 0.85
|  | Seismic Design:Design Code/Site Class/Import.Factor/Fa/Fv/Ss/S1 | [7 empty] | - | ASCE7-10/D/1.25/1/1.33/1.125/0.46
|  | Wind Design: Design Code/Wind Speed | [7 empty] | -/Km/hr | ASCE7-10 |  |  | / | 232
|  | Corrosion Allowance Sheel& Bottom / Roof / Structure | [7 empty] | mm |  | 1.6 | / | 1.6 |  | / | 1.6
|  | Design Liquid Level (H): | [7 empty] | mm | 2250
Materials
|  | Bottom /Fy /Class | [7 empty] | Mpa | A-283 Gr.C/103.4/0
|  | Roof/Fy /Class | [7 empty] | Mpa | A-283 Gr.C/103.4/0
|  | Shell/Fy/Class | [7 empty] | Mpa | A-283 Gr.C/103.4/0
2.2.3.1.3 ASTM A283, grade A steel is to be used only for nonstructural items such as clips, roof sheets, and other low-stressed components less than 1 in. (25 mm) thick. Grade B and C shell plates are limited to a thickness of 1 in. (25 mm) when tension stress governs and 1 ½ in. (38 mm) when compression stress governs. Grade D shell plates are limited to a thickness of ¾ in. (19 mm).

## Shell Thickness
NISOC | [7 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
شماره پیمان: | [7 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | 8 | از | 6 | شماره صفحه:
9184 – 073 - 053 | [7 empty] | BK |  | GCS |  | IDR | 120 | ME | CN | 0001 |  | V00
3)Shell Thickness
Shell Thickness Of The Tank As Per Para 3.7 & Table 3-14 Should Be Calculated As Follow:
|  |  | hTCL: |  | The height of liquid from top capacity level to the bottom of shell in Meter= | [11 empty] | 2.25 | m
|  |  | hp: |  | The height of liquid from top capacity level to the bottom of shell course being designed in Meter | [11 empty] | 2.25 | m
|  |  | hco1: |  | The height of shell course no.#1 in Meter | [11 empty] | 2 | m
|  |  | hco2: |  | The height of shell course no.#2 in Meter | [11 empty] | 0.6 | m
|  |  | D: |  | The nominal Tank Diameter in Meter | [11 empty] | 3.5 | m
|  |  | G: |  | Product Specific gravity ( 1 For water ) | [11 empty] | 1
|  |  | E: |  | Joint Efficiency | [11 empty] | 0.85
|  |  | S : |  | Allowable Design Stress @design temperature in Mpa | [11 empty] | 103.4 | Mpa
|  |  | C.A: |  | Corrosion Allowance Shell | [11 empty] | 1.6 | mm
[5 empty] | Corrosion Allowance Bottom | [11 empty] | 1.6 | mm
[5 empty] | Corrosion Allowance Roof | [11 empty] | 1.6 | mm
|  |  | td : |  | The required design shell plate thickness in Millimeter | [12 empty] | mm
3.1)Shell course no.#1 thickness calculation for design condition
|  |  | hco1: |  | The height of shell course no.#1 in Meter | [11 empty] | 2 | m
|  |  | hp1: |  | The height of liquid from top capacity level to the bottom of shellcourse no.#1 in Meter | [11 empty] | 2.25 | m
|  | td-co#1= |  |  | (4.9xhp1xDxG)/(SxE) |  |  |  |  | + | G= | [6 empty] | mm
2.039
|  | Minimum thickness as per section 3-10 & Table 16 is 6.35 millimeter + C.A. | [14 empty] | 7.95 | mm
3.2)Shell course no.#1 thickness calculation for test condition
|  |  | hco1: |  | The height of shell course no.#1 in Meter | [11 empty] | 2 | m
|  |  | hhtw1: |  | The height of hydrotest water from top of shell to the bottom of shell course no. 1 in Meter | [11 empty] | 2.25 | m
|  | tt-co#1= |  |  | (4.9xhhtw1xDxG)/(SxE) |  |  |  |  | + | G= | [5 empty] | 2.1073 | mm
[6 empty] | Selected thickness for co. no, #1 | [10 empty] | 8 | mm
3.3)Shell course no.#2 thickness calculation for design condition
|  | hco2: |  | The height of shell course no.#2 in Meter | [12 empty] | 0.6 | m
|  | hp2: |  | The height of hydrotest water from top of shell to the bottom of shell course no. #2 in Meter | [12 empty] | 0.25 | m
| td-co#2= |  |  | (4.9xhp1xDxG)/(SxE) |  |  |  |  | + | G= | [6 empty] | 1.6488 | mm
|  | Minimum thickness as per section 3-10 & Table 16 is 6.35 millimeter + C.A. | [14 empty] | 7.95 | mm
3.4)Shell course no.#2 thickness calculation for test condition
|  | hco2: |  | The height of shell course no.#2 in Meter | [12 empty] | 0.6 | m
|  | hhtw2: |  | The height of hydrotest water from top of shell to the bottom of shell course no. #2 in Meter | [12 empty] | 2.25 | m
| tt-co#2= |  |  | (4.9xhhtw1xDxG)/(SxE) |  |  |  |  | + | G= | [6 empty] | 2.1073 | mm
[7 empty] | Selected thickness for co. no, #2 | [9 empty] | 8 | mm

## Bottom & Roof Plate
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
شماره پیمان: | [5 empty] | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | 8 | از | 7 | شماره صفحه:
9184 – 073 - 053 | [5 empty] | BK | GCS | IDR | 120 | ME | CN | 0001 | V00
4)Bottom Plate
Minimum Thickness of bottom plate as per article 3-10 of AWWA -D100 -11 is 6.35 millimeter except corrosion allowance
| tb = |  | 7.95 |  | mm
|  | Selected thickness for Bottom Plates = | [5 empty] | 8 | mm
5)Roof Plate
Minimum Thickness of Roof plate as per article 3.10.2 of AWWA -D100 -11 is 4.76 millimeter except corrosion allowance
| tr= |  | 6.36 | mm
|  | Selected thickness for Bottom Plates = | [5 empty] | 8 | mm

## Loading
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید مخازن ذخیره گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0026_00 )
Mechanical Calculation Book For Elevated Potable Water Tank (TK-2209)
شماره پیمان: |  |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | 8 | از | 8 | شماره صفحه:
9184 – 073 - 053 |  |  |  | BK | GCS |  | IDR | 120 | ME |  | CN |  | 0001 |  | V00
6)Tank Capacity:
Maximum Tank Capacity Is The Volume Of Product In A Tank When The Tank Is Filled To Its Design Liquid Level As:
|  |  | Design Liquid Level (H): |  |  | 2.25 |  | m
|  |  | Tank Diameter (ID): |  |  | 3.5 |  | m
|  |  | Minimum Capacity |  |  | 21.6475 |  | m3
7)Water Load:
| ID |  | Inside Diameter Of Tank: |  |  | 3500 |  | mm
| Hs |  | Tank Shell Height: |  |  | 2600 |  | mm
| ID |  | Conical Bottom Diameter: |  |  | 3500 |  | mm
| α |  | Conical Bottom Angel: |  |  | 32 |  | º
| Hcl |  | Conical Bottom Height: |  |  | 1093.5214 |  | mm
| ro |  | Water Specific Gravity: |  |  | 1000 |  | Kg/m3
| Mw |  | Water mass: |  |  | 26907.9911 |  | kg
| Fwa |  | Water Load: |  |  | 263967.3929 |  | N
8)Snow Load
| β |  | Maximum Angel For The Roof |  |  | 17 |  | º
| Hcu |  | Conical Roof Height |  |  | 535.0287 |  | mm
| Ar |  | Surface Area Of The Roof Cone |  |  | 9.2007 |  | m2
| MSA |  | Minimum Snow Load |  |  | 1205 |  | N/m2 |  | AS PER CODE PARA 3.1.3.1
| MS |  | Snow Mass |  |  | 1131.3142 |  | kg
| Fs |  | Snow Load |  |  | 11086.8796 |  | N
9)Wind Load
| Pcy |  | Wind Pressure Load On Cylindrical |  |  | 18 |  | Ib/sq. ft | à | 862 |  | N/m2 |  |  |  | AS PER CODE PARA 3.1.4
| Pco |  | Wind Pressure Load On Cones |  |  | 15 |  | Ib/sq. ft | à | 718 |  | N/m2 |  |  |  | AS PER CODE PARA 3.1.4
| Wv |  | Wind Velocity |  |  | 232 |  | Km/hr | à | 64.96 |  | m/s | à | 145.5104 | mph
| Acy |  | Projected Areas Of Cylinder Shell |  |  | 9.1 |  | m2
| Acu |  | Projected Areas Of Upper Cone |  |  | 1.8726 |  | m2
| Acl |  | Projected Areas Of Lower Cone |  |  | 3.8273 |  | m2
| Fwi |  | Total Force Act On Tank |  |  | 11936.7463 |  | N |  | This Force Act On The Center Of Gravity Of The Tank | [5 empty] | (PARA 3.1.4.2)
10) Body Load
|  |  | 10.1)Shall Weight= |  |  | 1795.3574 |  | kg | à |  | 17612.4558 |  | N
|  |  | 10.2)Bottom Weight= |  |  | 240.356 |  | kg | à |  | 2357.8923 |  | N
|  |  | 10.3)Roof Weight= |  |  | 117.5993 |  | kg | à |  | 1153.6492 |  | N
|  |  |  | Sum: |  | 2153.3127 |  | kg | à |  | 21123.9973 |  | N