| طرح نگهداشت و افزایش تولید 27 مخزن |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| ROOF STRUCTURE CALCULATION FOR FIRE WATER TANKS (TK-2301 A/B) نگهداشت و افزایش تولید میدان نفتی بینک |  |  |  |  |  |  |  |
| V02 | Mar. 2025 | IFI | IDR | M.Fakharian | S.Faramarzpour |  |
| V01 | Dec. 2024 | IFI | IDR | M.Fakharian | S.Faramarzpour |  |
| V00 | NOV. 2024 | IFI | IDR | M.Fakharian | M.Sadeghian |  |
| Rev. | Date | Purpose of Issue/Status | Prepared by: | Checked by: | Approved by: | CLIENT Approval |
| Status: | IFA: Issued For Approval IFI: Issued For Information AFC: Approved For Construction |  |  |  |  |  |

REVISION RECORD SHEET

| PAGE | V00 | V01 | V02 | V03 | V04 |  | PAGE | V00 | V01 | V02 | V03 | V04 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | X | X | X |  |  |  | 66 |  |  |  |  |  |
| 2 | X | X | X |  |  |  | 67 |  |  |  |  |  |
| 3 | X | X | X |  |  |  | 68 |  |  |  |  |  |
| 4 | X | X | X |  |  |  | 69 |  |  |  |  |  |
| 5 | X | X | X |  |  |  | 70 |  |  |  |  |  |
| 6 | X | X | X |  |  |  | 71 |  |  |  |  |  |
| 7 | X | X | X |  |  |  | 72 |  |  |  |  |  |
| 8 | X | X | X |  |  |  | 73 |  |  |  |  |  |
| 9 | X | X | X |  |  |  | 74 |  |  |  |  |  |
| 10 | X | X | X |  |  |  | 75 |  |  |  |  |  |
| 11 | X | X | X |  |  |  | 76 |  |  |  |  |  |
| 12 |  | X | X |  |  |  | 77 |  |  |  |  |  |
| 13 |  | X | X |  |  |  | 78 |  |  |  |  |  |
| 14 |  | X | X |  |  |  | 79 |  |  |  |  |  |
| 15 |  | X | X |  |  |  | 80 |  |  |  |  |  |
| 16 |  | X | X |  |  |  | 81 |  |  |  |  |  |
| 17 |  | X | X |  |  |  | 82 |  |  |  |  |  |
| 18 |  |  | X |  |  |  | 83 |  |  |  |  |  |
| 19 |  |  | X |  |  |  | 84 |  |  |  |  |  |
| 20 |  |  | X |  |  |  | 85 |  |  |  |  |  |
| 21 |  |  | X |  |  |  | 86 |  |  |  |  |  |
| 22 |  |  | X |  |  |  | 87 |  |  |  |  |  |
| 23 |  |  | X |  |  |  | 88 |  |  |  |  |  |
| 24 |  |  |  |  |  |  | 89 |  |  |  |  |  |
| 25 |  |  |  |  |  |  | 90 |  |  |  |  |  |
| 26 |  |  |  |  |  |  | 91 |  |  |  |  |  |
| 27 |  |  |  |  |  |  | 92 |  |  |  |  |  |
| 28 |  |  |  |  |  |  | 93 |  |  |  |  |  |
| 29 |  |  |  |  |  |  | 94 |  |  |  |  |  |
| 30 |  |  |  |  |  |  | 95 |  |  |  |  |  |
| 31 |  |  |  |  |  |  | 96 |  |  |  |  |  |
| 32 |  |  |  |  |  |  | 97 |  |  |  |  |  |
| 33 |  |  |  |  |  |  | 98 |  |  |  |  |  |
| 34 |  |  |  |  |  |  | 99 |  |  |  |  |  |
| 35 |  |  |  |  |  |  | 100 |  |  |  |  |  |
| 36 |  |  |  |  |  |  | 101 |  |  |  |  |  |
| 37 |  |  |  |  |  |  | 102 |  |  |  |  |  |
| 38 |  |  |  |  |  |  | 103 |  |  |  |  |  |
| 39 |  |  |  |  |  |  | 104 |  |  |  |  |  |
| 40 |  |  |  |  |  |  | 105 |  |  |  |  |  |
| 41 |  |  |  |  |  |  | 106 |  |  |  |  |  |
| 42 |  |  |  |  |  |  | 107 |  |  |  |  |  |
| 43 |  |  |  |  |  |  | 108 |  |  |  |  |  |
| 44 |  |  |  |  |  |  | 109 |  |  |  |  |  |
| 45 |  |  |  |  |  |  | 110 |  |  |  |  |  |
| 46 |  |  |  |  |  |  | 111 |  |  |  |  |  |
| 47 |  |  |  |  |  |  | 112 |  |  |  |  |  |
| 48 |  |  |  |  |  |  | 113 |  |  |  |  |  |
| 49 |  |  |  |  |  |  | 114 |  |  |  |  |  |
| 50 |  |  |  |  |  |  | 115 |  |  |  |  |  |
| 51 |  |  |  |  |  |  | 116 |  |  |  |  |  |
| 52 |  |  |  |  |  |  | 117 |  |  |  |  |  |
| 53 |  |  |  |  |  |  | 118 |  |  |  |  |  |
| 54 |  |  |  |  |  |  | 119 |  |  |  |  |  |
| 55 |  |  |  |  |  |  | 120 |  |  |  |  |  |
| 56 |  |  |  |  |  |  | 121 |  |  |  |  |  |
| 57 |  |  |  |  |  |  | 122 |  |  |  |  |  |
| 58 |  |  |  |  |  |  | 123 |  |  |  |  |  |
| 59 |  |  |  |  |  |  | 124 |  |  |  |  |  |
| 60 |  |  |  |  |  |  | 125 |  |  |  |  |  |
| 61 |  |  |  |  |  |  | 126 |  |  |  |  |  |
| 62 |  |  |  |  |  |  | 127 |  |  |  |  |  |
| 63 |  |  |  |  |  |  | 128 |  |  |  |  |  |
| 64 |  |  |  |  |  |  | 129 |  |  |  |  |  |
| 65 |  |  |  |  |  |  | 130 |  |  |  |  |  |

CONTENTS

1.0	INTRODUCTION	4

2.0	USING CODES:	Error! Bookmark not defined.

3.0	TRIAL SIZING:	Error! Bookmark not defined.

4.0	LOADING:	Error! Bookmark not defined.

5.0	STRUCTURE ANALYSIS:	Error! Bookmark not defined.

6.0	STRUCTURE DESIGN:	Error! Bookmark not defined.

Input Design Data:	Error! Bookmark not defined.

Out Put Design Data:	Error! Bookmark not defined.

- INTRODUCTION

Binak oilfield in Bushehr province is a part of the southern oilfields of Iran, is located 20 km northwest of Genaveh city.

With the aim of increasing production of oil from Binak oilfield, an EPC/EPD Project has been defined by NIOC/NISOC and awarded to Petro Iran Development Company (PEDCO). Also PEDCO (as General Contractor) has assigned the EPC-packages of the Project to "Hirgan Energy - Design and Inspection" JV.

GENERAL DEFINITION

The following terms shall be used in this document.

| CLIENT: | National Iranian South Oilfields Company (NISOC) |
| --- | --- |
| PROJECT: | Binak Oilfield Development – SUPPLY STORAGE TANK |
| EPD/EPC CONTRACTOR (GC): | Petro Iran Development Company (PEDCO) |
| EPC CONTRACTOR: | Joint Venture of : Hirgan Energy – Design & Inspection(D&I) Companies |
| VENDOR: | IDRIL KHAVARMIANEH (IDR) |
| EXECUTOR: | Executor is the party which carries out all or part of construction and/or commissioning for the project. |
| THIRD PARTY INSPECTOR (TPI): | Third Party Inspector |
| SHALL: | Is used where a provision is mandatory. |
| SHOULD: | Is used where a provision is advisory only. |
| WILL: | Is normally used in connection with the action by CLIENT rather than by an EPC/EPD CONTRACTOR, supplier or VENDOR. |
| MAY: | Is used where a provision is completely discretionary. |

- USING CODES:

The codes, used for analysis and design of this Structure are:

- AISC-360-10-ASD for Steel Design

- API 650-2021 (Welded Tanks for Oil Storage)

- MECHANICAL GA For Fire Water Tank 2031A

- National Building Regulations- Topic 10

- 2800 Code for seismic design of buildings

- National Building Regulations- Topic 6

- Iranian Seismic Design Code for Oil industries (3nd Edition)-1395 (Pub No.38)

- TRIAL SIZING:

- Roof type: Cone Tank Diameter: ID 13.0 m

- Tank Height: 				9.5 m

- Roof ceiling Slope:			5.7’≡10%

- Roof Ceiling Thk.:			8 mm

- No. Of Beam:				24

- Beam Section :			IPE 160

- Lateral Beam Section:		L80x8

- LOADING:

The design loads applied for structural analysis include Dead load, Live load, wind load and Seismic load.

A) Dead Load:

AI) Ceiling:

1-Roof:

Plate 8 mm

AII) Structure

SAP2000 Software has considered weight of structural members automatically.

B) Snow Load(S):

1-Roof:		Pr=IsCnChCsPs=23.7

(Binak) 	Ps=25 kgm2;

Is=1.2;	Cn=0.8;	Cs=0.989;	Ch=1.0

B) Live Load (LLr):

L.L=100     	According to API 650 - Edition 2021

C) Asymmetric Snow Load:

According to National Building Regulations- Topic 6

- α=5.7’ ≡10% ≥ 4%

hd=0.123lu4100Ps+50-0.5=0.34 m	lu=6.5 m

83hdi=2.87 m	i=0.1		γ=0.43Ps+2.2=2.3075

hdγi=0.248 KNm2	hdγi+Pr=48.5 kgm2		0.3Pr=7.11  kgm2

S1=7.11× (0.29~1.7) = (2.06~12.09)

S2=23.7× (1.04~1.7) = (24.65~40.29)

S3=48.5× (0.29~1.04) = (14.07~50.44)

D) Wind Load:

Wind loads have been calculated according to:

;	V=120 km/hr;

According to National Building Regulations-Topic 6

;

;

For any Direction:

;

For any Direction:

P2E=68×1.2×1.0×-2= -163.2 kg/m²	(0.29 m to 1.7 m) 	P2E= (47.3-277.4)

P3E=68×1.2×1.0×-1.0= -81.6 kg/m²;	(0.29 m to 1.7 m)	P3E= (23.7-138.7)

Finally total loads would be as below:

These wind loads have been applied to roof structural members in sap2000 model with respect to their share of roof area.

E) Seismic Load:

Earthquake loads have been calculated according to 038 & API650 13 ED. Code for seismic design of buildings:

Seismic Use Group: 	III

Soil Type:		IV	(Worst Case)

Important factor (I):	1.5

Scaling Factor (Q)	1.0

Ai= SDSI/R

S1=0.46	Ss=1.125

SDS=0.75		SD1=0.41

T0=0.2 SD1/ SDS=0.11		Ts= SD1/ SDS=0.546

T0 < T=0.3 < Ts	SA=SDS

R=3.5		Ai= SDSI/R=0.32

: Weight of building which participate in earthquake.

Earthquake loads have been calculated according to 2800 Code for seismic design of buildings:

Soil Type:		IV	Ts=1.0		T0=0.15	T=0.05H0.75=0.3

Important factor (I):	1.4

S0=1.1		S=1.75		Iw=1.4		B1=1+S=2.75

C=ABI/R=0.3×2.75×1.4/3.5=0.33

Vumin=1.6AIW/Ru:	Ru=3.5		Vumin=0.224W		Cmin=0.224

Vertical Seismic Load:	(Bay=13 m<15 m → Not Needed)

Ev=0.6AI × (W) =0.252W (According to 2800)

These seismic loads have been applied to all points in sap2000 model automatically by sap2000 program.

Tank Sizing:

- Roof type: Cone Tank Diameter: ID 13.0 m

- Tank Height: 				9.5 m

- Roof ceiling Slope:			5.7’≡10%

- Roof Ceiling Thk.:			8 mm

- No. Of Beam:				24

- Beam Section :			IPE 160

- Lateral Beam Section:		L80x8

- STRUCTURE ANALYSIS:

The 3-dimensional structural analysis will be performed using “SAP 2000 V. 19”

  - General Input Data:

Table:  Coordinate Systems

| Table: Coordinate Systems |  |  |
| --- | --- | --- |
| Name | Type | X |  | Y | Z | AboutZ | AboutY | AboutX |
|  |  | m |  | m | m | Degrees | Degrees | Degrees |
| GLOBAL | Cylindrical | 0. |  | 0. | 0. | 0. | 0. | 0. |

Table:  Grid Lines

|  |  |  |  |  |  | Table: Grid Lines, |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Coord Sys |  | Axis Dir | Grid ID |  | XRYZ Coord |  | TAngle | LineType | Line Color |  | Visible | Bubble Loc | All Visible | Bubble Size |
|  |  |  |  |  | m |  | Degrees |  |  |  |  |  |  | m |
| GLOBAL |  | R | A |  | 0. |  |  | Primary | 10461087 |  | Yes | End | Yes | 0.25 |
| GLOBAL |  | R | B |  | 1.1 |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | R | E |  | 3.26 |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | R | C |  | 4.88 |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | R | D |  | 6.5 |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 1 |  |  |  | 0. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 2 |  |  |  | 15. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 3 |  |  |  | 30. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 4 |  |  |  | 45. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 5 |  |  |  | 60. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 6 |  |  |  | 75. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 7 |  |  |  | 90. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 8 |  |  |  | 105. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 9 |  |  |  | 120. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 10 |  |  |  | 135. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 11 |  |  |  | 150. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 12 |  |  |  | 165. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 13 |  |  |  | 180. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 14 |  |  |  | 195. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 15 |  |  |  | 210. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 16 |  |  |  | 225. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 17 |  |  |  | 240. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 18 |  |  |  | 255. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 19 |  |  |  | 270. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 20 |  |  |  | 285. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 21 |  |  |  | 300. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 22 |  |  |  | 315. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 23 |  |  |  | 330. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | T | 24 |  |  |  | 345. | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | Z | Z1 |  | 0. |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | Z | Z2 |  | 0.195 |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | Z | Z2.1 |  | 0.39 |  |  | Primary | 10461087 |  | Yes | End |  |  |
| GLOBAL |  | Z | Z3 |  | 0.65 |  |  | Primary | 10461087 |  | Yes | End |  |  |

Table:  Material Properties 03a - Steel Data,

|  |  |  | Table: Material Properties 03a - |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Material |  | Fy |  | Fu | EffFy | EffFu | SSCurve Opt |  | SSHys Type | SHard | SMax | SRup | FinalSlope |
|  |  | Kgf/m2 |  | Kgf/m2 | Kgf/m2 | Kgf/m2 |  |  |  |  |  |  |  |
| ST37 |  | 24000000. |  | 37000000. | 24000000. | 37000000. | Simple |  | Kinematic | 0.02 | 0.14 | 0.2 | -0.1 |

Table:  Frame Section Properties 01 - General, Part 1 of 5

| Table: Frame Section Properties 01 - General, Part 1 of 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Section Name | Material | Shape | t3 | t2 | tf |  | tw |  | t2b |  | tfb |  | Area |  | Tors Const |  | I33 |
|  |  |  | m | m | m |  | m |  | m |  | m |  | m2 |  | m4 |  | m4 |
| B1 | ST37 | SD Section |  |  |  |  |  |  |  |  |  |  | 0.0092 |  | 0.000088 |  | 0.000047 |
| IPE160 | ST37 | I/Wide Flange | 0.16 | 0.082 | 0.0074 |  | 0.005 |  | 0.082 |  | 0.0074 |  | 0.00201 |  | 3.540E-08 |  | 8.690E-06 |
| L80X8 | ST37 | Angle | 0.08 | 0.08 | 0.008 |  | 0.008 |  |  |  |  |  | 0.001227 |  | 2.594E-08 |  | 7.224E-07 |

Table:  Frame Section Properties 01 - General, Part 2 of 5

| Section Name | I22 | I23 | AS2 | AS3 | S33 | S22 | Z33 | Z22 | R33 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | m4 | m4 | m2 | m2 | m3 | m3 | m3 | m3 | m |
| B1 | 0.000085 | 0. | 0.003284 | 0.006096 | 0.000468 | 0.000635 | 0.000544 | 0.000788 | 0.071322 |
| IPE160 | 6.830E-07 | 0. | 0.0008 | 0.001011 | 0.000109 | 0.000017 | 0.000124 | 0.000026 | 0.065752 |
| L80X8 | 7.224E-07 | 4.365E-07 | 0.00064 | 0.00064 | 0.000013 | 0.000013 | 0.000023 | 0.000023 | 0.024264 |

Table:  Frame Section Properties 01 - General, Part 4 of 5

| Table: Frame Section Properties 01 - General, Part 4 of 5 |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Section Name | R22 | Conc Col | Conc Beam | Color | Total Wt |  | Total Mass |  | From File |  | A Mod |  | A2 Mod |  | A3 Mod | J Mod |
|  | m |  |  |  | Kgf |  | Kgf-s2/m |  |  |  |  |  |  |  |  |  |
| B1 | 0.095848 | No | No | Red | 497.72 |  | 50.75 |  | No |  | 1. |  | 1. |  | 1. | 1. |
| IPE160 | 0.018434 | No | No | Magenta | 2059.65 |  | 210.03 |  | Yes |  | 1. |  | 1. |  | 1. | 1. |
| L80X8 | 0.024264 | No | No | White | 491.22 |  | 50.09 |  | Yes |  | 1. |  | 1. |  | 1. | 1. |

Table:  Frame Section Properties 01 - General, Part 5 of 5

| Section Name | I2 Mod | I3 Mod | M Mod | W Mod | SectIn File | FileName | GUID | Notes |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| B1 | 1. | 1. | 1. | 1. |  |  |  | Added 3/29/2017 11:02:44 AM |
| IPE160 | 1. | 1. | 1. | 1. | IPE160 | c:\program files\computers and structures\sap2000 19\euro.pro |  | Imported 3/29/2017 12:37:25 PM from Euro.pro |
| L80X8 | 1. | 1. | 1. | 1. | L80X8 | c:\program files\computers and structures\sap2000 19\euro.pro |  | Imported 3/29/2017 12:37:48 PM from Euro.pro |

Table:  Area Section Properties, Part 1 of 3

| Table: Area Section Properties, Part 1 of 3 |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Section | Material | Mat Angle | Area Type | Type |  | Drill DOF | Thickness |  | Bend Thick | Arc | In Comp | Coord Sys |
|  |  | Degrees |  |  |  |  | m |  | m | Degrees |  |  |
| Roof Shell | ST37 | 0. | Shell | Shell-Thin |  | Yes | 0.008 |  | 0.008 |  |  |  |

Table:  Area Section Properties, Part 2 of 3

| Section | Color | Total Wt | Total Mass | F11 Mod | F22 Mod | F12 Mod | M11 Mod | M22 Mod | M12 Mod | V13 Mod | V23 Mod | MMod | WMod |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  | Kgf | Kgf-s2/m |  |  |  |  |  |  |  |  |  |  |
| Roof Shell | Yellow | 8063.47 | 822.24 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 0.01 | 1. | 1. | 1. | 1. |

Table:  Area Section Properties, Part 3 of 3

| Table: Area Section Properties, Part 3 of 3 |  |  |
| --- | --- | --- |
| Section | GUID | Notes |
| Roof Shell |  | Added 2008/01/06 01:34:38 ?.? |

Table:  Load Pattern Definitions

| Table: Load Pattern Definitions |  |
| --- | --- |
| LoadPat | Design Type |  | Self WtMult | AutoL oad | GUID | Notes |
| DEAD | Dead |  | 1. |  |  |  |
| LL | Live |  | 0. |  |  |  |
| WIND | Wind |  | 0. | None |  |  |
| Snow(asymmetric) | Snow |  | 0. |  | aeef0373-9b98-4d99-b7a1-dcaac379e965 |  |
| Temp.(+) | Temperature |  | 0. |  | 44417da3-c2fc-4bfe-b219-b86b39c398ca |  |
| EQ | Quake |  | 0. | USER COEFF | db46d43c-7d7b-406a-b0c4-728182458b82 |  |
| Temp.(-) | Temperature |  | 0. |  | d826c701-cd22-43ec-84aa-43bd382e9575 |  |
| EQ(V) | Other |  | 0.252 |  | 980ede88-2c1c-42b1-bbaa-0b30ecc947ad |  |

Table:  Case - Static 1 - Load Assignments

| Table: Case - Static 1 - Load Assignments |  |  |  |
| --- | --- | --- | --- |
| Case | LoadType | LoadName | LoadSF |
| DEAD | Load pattern | DEAD | 1. |
| WIND | Load pattern | WIND | 1. |
| LIVE | Load pattern | LL | 1. |
| LIVE | Load pattern | LL | 1. |
| LL(asymmetric) | Load pattern | Snow(asymmetric) | 1. |
| Temp.(+) | Load pattern | Temp.(+) | 1. |
| EQ | Load pattern | EQ | 1. |
| Temp.(-) | Load pattern | Temp.(-) | 1. |
| EQ(V) | Load pattern | EQ(V) | 1. |

Table:  Load Case Definitions, Part 1 of 2

| Table: Load Case Definitions, Part 1 of 2 |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Case | Type | Initial Cond | Modal Case |  | Base Case | Mass Source |  | Des TypeOpt |  | Design Type | Des ActOpt | Design Act |
| DEAD | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Dead | Prog Det | Non-Composite |
| MODAL | LinModal | Zero |  |  |  |  |  | Prog Det |  | Other | Prog Det | Other |
| WIND | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Wind | Prog Det | Short-Term Composite |
| LIVE | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Live | Prog Det | Short-Term Composite |
| LL(asymmetric) | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Snow | Prog Det | Short-Term Composite |
| Temp.(+) | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Temperature | Prog Det | Short-Term Composite |
| EQ | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Quake | Prog Det | Short-Term Composite |
| Temp.(-) | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Temperature | Prog Det | Short-Term Composite |
| EQ(V) | LinStatic | Zero |  |  |  |  |  | Prog Det |  | Other | Prog Det | Other |

Table:  Load Case Definitions, Part 2 of 2

| Case | Auto Type | Run Case | Case Status | GUID | Notes |
| --- | --- | --- | --- | --- | --- |
| DEAD | None | Yes | Finished |  |  |
| MODAL | None | Yes | Finished |  |  |
| WIND | None | Yes | Finished |  |  |
| LIVE | None | Yes | Finished |  |  |
| LL(asymmetric) | None | Yes | Finished | 832c8f9c-a30d-4be5-a81e-8f5312ff9a26 |  |
| Temp.(+) | None | Yes | Finished | d745dd9f-4da3-4517-a618-f9690fede060 |  |
| EQ | None | Yes | Finished | cf38ebd5-59dd-466d-a44c-c6de0ad746a7 |  |
| Temp.(-) | None | Yes | Finished | f8930cf6-ac23-49bd-bf51-c3c239085e05 |  |
| EQ(V) | None | Yes | Finished | 64cd170c-b5d1-4275-8038-c69bc1625fca |  |

Table:  Auto Seismic - User Coefficient

| Table: Auto Seismic - User Coefficient, |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Load Pat | Dir | Percent Ecc | Ecc Override | UserZ | C |  | K | Weight Used |  | Base Shear |
|  |  |  |  |  |  |  |  | Kgf |  | Kgf |
| EQ | X | 0.05 | No | No | 0.35 |  | 1. | 12907.99 |  | 4517.8 |

Table:  Mass Source

| Table: Mass Source |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| MassSource | Elements | Masses | Loads | IsDefault | LoadPat | Multiplier |
| MSSSRC1 | No | No | Yes | Yes | DEAD | 1. |
| MSSSRC1 |  |  |  |  | LL | 0.4 |

Table:  Combination Definitions,

|  |  |  | Table: Combination Definitions |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Combo Name |  | Combo Type |  | Auto Design |  | Case Type | Case Name |  | Scale Factor | Steel Design | Notes |
| UDSTL1 |  | Linear Add |  | No |  | Linear Static | DEAD |  | 1.4 | Strength | Dead Only; Strength |
| UDSTL2 |  | Linear Add |  | No |  | Linear Static | DEAD |  | 1.2 | Strength | Dead + Live + Snow (Partial); Strength |
| UDSTL2 |  |  |  |  |  | Linear Static | LIVE |  | 1.6 |  |  |
| UDSTL2 |  |  |  |  |  | Linear Static | LL(asymmetric) |  | 0.5 |  |  |
| UDSTL3 |  | Linear Add |  | No |  | Linear Static | DEAD |  | 1.2 | Strength | Dead + Live + Snow; Strength |
| UDSTL3 |  |  |  |  |  | Linear Static | LL(asymmetric) |  | 1.6 |  |  |
| UDSTL3 |  |  |  |  |  | Linear Static | LIVE |  | 1. |  |  |
| UDSTL4 |  | Linear Add |  | No |  | Linear Static | DEAD |  | 1.2 | Strength |  |
| UDSTL4 |  |  |  |  |  | Linear Static | LL(asymmetric) |  | 1.6 |  |  |
| UDSTL4 |  |  |  |  |  | Linear Static | WIND |  | 0.8 |  |  |
| UDSTL5 |  | Linear Add |  | No |  | Linear Static | DEAD |  | 1.2 | Strength |  |
| UDSTL5 |  |  |  |  |  | Linear Static | LL(asymmetric) |  | 0.5 |  |  |
| UDSTL5 |  |  |  |  |  | Linear Static | WIND |  | 1.6 |  |  |
| UDSTL5 |  |  |  |  |  | Linear Static | LIVE |  | 1. |  |  |
| UDSTL9 |  | Linear Add |  | No |  | Linear Static | DEAD |  | 1.2 | Strength | Dead (min) - Wind; Strength |
| UDSTL9 |  |  |  |  |  | Linear Static | EQ |  | -1. |  |  |
| UDSTL9 |  |  |  |  |  | Linear Static | LIVE |  | 1. |  |  |
| UDSTL9 |  |  |  |  | Linear Static |  | EQ(V) |  | 1. |  |  |
| UDSTL8 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 0.9 | Strength | Dead + Live + Static Earthquake; Strength |
| UDSTL8 |  |  |  |  | Linear Static |  | EQ |  | 1. |  |  |
| UDSTL8 |  |  |  |  | Linear Static |  | EQ(V) |  | 1. |  |  |
| UDSTL6 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 1.2 | Strength | Dead + Live - Static Earthquake; Strength |
| UDSTL6 |  |  |  |  | Linear Static |  | LL(asymmetric) |  | 0.2 |  |  |
| UDSTL6 |  |  |  |  | Linear Static |  | EQ |  | 1. |  |  |
| UDSTL6 |  |  |  |  | Linear Static |  | EQ(V) |  | 1. |  |  |
| UDSTL6 |  |  |  |  | Linear Static |  | LIVE |  | 1. |  |  |
| UDSTL7 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 0.9 | Strength | Dead + Live + Snow (Partial); Strength |
| UDSTL7 |  |  |  |  | Linear Static |  | WIND |  | 1.6 |  |  |
| UDSTL10 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 1.2 | Strength | Dead + Live + Snow (Partial); Strength |
| UDSTL10 |  |  |  |  | Linear Static |  | LIVE |  | 1.6 |  |  |
| UDSTL10 |  |  |  |  | Linear Static |  | Temp.(+) |  | 1. |  |  |
| UDSTL10 |  |  |  |  | Linear Static |  | LL(asymmetric) |  | 1.6 |  |  |
| UDSTL11 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 1.2 | Strength | Dead + Live + Snow (Partial); Strength |
| UDSTL11 |  |  |  |  | Linear Static |  | LIVE |  | 0.5 |  |  |
| UDSTL11 |  |  |  |  | Linear Static |  | Temp.(-) |  | 1.2 |  |  |
| UDSTL11 |  |  |  |  | Linear Static |  | LL(asymmetric) |  | 0.5 |  |  |
| UDSTL12 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 1.2 | Strength | Dead + Live + Snow (Partial); Strength |
| UDSTL12 |  |  |  |  | Linear Static |  | LIVE |  | 1.6 |  |  |
| UDSTL12 |  |  |  |  | Linear Static |  | Temp.(-) |  | 1. |  |  |
| UDSTL12 |  |  |  |  | Linear Static |  | LL(asymmetric) |  | 1.6 |  |  |
| UDSTL13 |  | Linear Add |  | No | Linear Static |  | DEAD |  | 1.2 | Strength | Dead + Live + Snow (Partial); Strength |
| UDSTL13 |  |  |  |  | Linear Static |  | LIVE |  | 0.5 |  |  |
| UDSTL13 |  |  |  |  | Linear Static |  | Temp.(+) |  | 1.2 |  |  |
| UDSTL13 |  |  |  |  | Linear Static |  | LL(asymmetric) |  | 0.5 |  |  |

- STRUCTURE DESIGN:

# DESIGN:

Steel structure design has performed according to AISC-360-10 by SAP2000 program.

# Input Design Data:

- K-Value (Effective Length Factor)

K-Value used for determining column slenderness. K-Value of columns and rafters for braced frame direction has taken 1.0.

# Out Put Design Data:

Table:  Steel Design 1 - Summary Data - AISC 360-10

|  |  |  |  |  |  |  | Table: Steel Design 1 - Summary Data - AISC 360-10, |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Frame |  | Design Sect |  | Design Type |  | Status |  | Ratio | Ratio Type | Combo | Location | ErrMsg |  | WarnMsg |
|  |  |  |  |  |  |  |  |  |  |  | m |  |  |  |
| 26 |  | B1 |  | Beam |  | No Messages |  | 0.272933 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 27 |  | B1 |  | Beam |  | No Messages |  | 0.274187 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 28 |  | B1 |  | Beam |  | No Messages |  | 0.275995 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 29 |  | B1 |  | Beam |  | No Messages |  | 0.277941 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 30 |  | B1 |  | Beam |  | No Messages |  | 0.280494 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 31 |  | B1 |  | Beam |  | No Messages |  | 0.281632 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 32 |  | B1 |  | Beam |  | No Messages |  | 0.280021 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 33 |  | B1 |  | Beam |  | No Messages |  | 0.274572 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 34 |  | B1 |  | Beam |  | No Messages |  | 0.266473 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 35 |  | B1 |  | Beam |  | No Messages |  | 0.261601 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 36 |  | B1 |  | Beam |  | No Messages |  | 0.259172 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 37 |  | B1 |  | Beam |  | No Messages |  | 0.257872 | PMM | UDSTL10 | 0. | No Messages |  | No Messages |
| 38 |  | B1 |  | Beam |  | No Messages |  | 0.257872 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 39 |  | B1 |  | Beam |  | No Messages |  | 0.259172 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 40 |  | B1 |  | Beam |  | No Messages |  | 0.261601 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 41 |  | B1 |  | Beam |  | No Messages |  | 0.266473 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 42 |  | B1 |  | Beam |  | No Messages |  | 0.274572 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 43 |  | B1 |  | Beam |  | No Messages |  | 0.280021 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 44 |  | B1 |  | Beam |  | No Messages |  | 0.281632 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 45 |  | B1 |  | Beam |  | No Messages |  | 0.280494 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 46 |  | B1 |  | Beam |  | No Messages |  | 0.277941 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 47 |  | B1 |  | Beam |  | No Messages |  | 0.275995 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 48 |  | B1 |  | Beam |  | No Messages |  | 0.274187 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 49 |  | B1 |  | Beam |  | No Messages |  | 0.272933 | PMM | UDSTL10 | 0.28716 | No Messages |  | No Messages |
| 50 |  | IPE160 |  | Brace |  | No Messages |  | 0.769684 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 51 |  | IPE160 |  | Brace |  | No Messages |  | 0.761548 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 52 |  | IPE160 |  | Brace |  | No Messages |  | 0.76079 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 53 |  | IPE160 |  | Brace |  | No Messages |  | 0.761548 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 54 |  | IPE160 |  | Brace |  | No Messages |  | 0.769684 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 55 |  | IPE160 |  | Brace |  | No Messages |  | 0.772581 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 56 |  | IPE160 |  | Brace |  | No Messages |  | 0.776484 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 57 |  | IPE160 |  | Brace |  | No Messages |  | 0.78144 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 58 |  | IPE160 |  | Brace |  | No Messages |  | 0.787326 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 59 |  | IPE160 |  | Brace |  | No Messages |  | 0.794203 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 60 |  | IPE160 |  | Brace |  | No Messages |  | 0.830167 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 61 |  | IPE160 |  | Brace |  | No Messages |  | 0.835568 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 62 |  | IPE160 |  | Brace |  | No Messages |  | 0.839369 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 63 |  | IPE160 |  | Brace |  | No Messages |  | 0.813101 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 64 |  | IPE160 |  | Brace |  | No Messages |  | 0.812935 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 65 |  | IPE160 |  | Brace |  | No Messages |  | 0.813101 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 66 |  | IPE160 |  | Brace |  | No Messages |  | 0.839369 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 67 |  | IPE160 |  | Brace |  | No Messages |  | 0.835568 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 68 |  | IPE160 |  | Brace |  | No Messages |  | 0.830167 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 69 |  | IPE160 |  | Brace |  | No Messages |  | 0.794203 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 70 |  | IPE160 |  | Brace |  | No Messages |  | 0.787326 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 71 |  | IPE160 |  | Brace |  | No Messages |  | 0.78144 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 72 |  | IPE160 |  | Brace |  | No Messages |  | 0.776484 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 73 |  | IPE160 |  | Brace |  | No Messages |  | 0.772581 | PMM | UDSTL12 | 1.63169 | No Messages |  | No Messages |
| 9 |  | L80X8 |  | Beam |  | No Messages |  | 0.493249 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 10 |  | L80X8 |  | Beam |  | No Messages |  | 0.495601 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 11 |  | L80X8 |  | Beam |  | No Messages |  | 0.498572 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 12 |  | L80X8 |  | Beam |  | No Messages |  | 0.502017 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 13 |  | L80X8 |  | Beam |  | No Messages |  | 0.50576 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 14 |  | L80X8 |  | Beam |  | No Messages |  | 0.509573 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 15 |  | L80X8 |  | Beam |  | No Messages |  | 0.513089 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 16 |  | L80X8 |  | Beam |  | No Messages |  | 0.51595 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 17 |  | L80X8 |  | Beam |  | No Messages |  | 0.51796 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 18 |  | L80X8 |  | Beam |  | No Messages |  | 0.518998 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 19 |  | L80X8 |  | Beam |  | No Messages |  | 0.518998 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 20 |  | L80X8 |  | Beam |  | No Messages |  | 0.51796 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 21 |  | L80X8 |  | Beam |  | No Messages |  | 0.51595 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 22 |  | L80X8 |  | Beam |  | No Messages |  | 0.513089 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 23 |  | L80X8 |  | Beam |  | No Messages |  | 0.509573 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 24 |  | L80X8 |  | Beam |  | No Messages |  | 0.50576 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 25 |  | L80X8 |  | Beam |  | No Messages |  | 0.502017 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 74 |  | L80X8 |  | Beam |  | No Messages |  | 0.498572 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 75 |  | L80X8 |  | Beam |  | No Messages |  | 0.495601 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 76 |  | L80X8 |  | Beam |  | No Messages |  | 0.493249 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 77 |  | L80X8 |  | Beam |  | No Messages |  | 0.491622 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 78 |  | L80X8 |  | Beam |  | No Messages |  | 0.490791 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 79 |  | L80X8 |  | Beam |  | No Messages |  | 0.490791 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 80 |  | L80X8 |  | Beam |  | No Messages |  | 0.491622 | PMM | UDSTL10 | 0.42552 | No Messages |  | No Messages |
| 81 |  | L80X8 |  | Beam |  | No Messages |  | 0.588918 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 82 |  | L80X8 |  | Beam |  | No Messages |  | 0.590814 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 83 |  | L80X8 |  | Beam |  | No Messages |  | 0.593291 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 84 |  | L80X8 |  | Beam |  | No Messages |  | 0.59631 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 85 |  | L80X8 |  | Beam |  | No Messages |  | 0.599821 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 86 |  | L80X8 |  | Beam |  | No Messages |  | 0.603794 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 87 |  | L80X8 |  | Beam |  | No Messages |  | 0.607547 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 88 |  | L80X8 |  | Beam |  | No Messages |  | 0.610398 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 89 |  | L80X8 |  | Beam |  | No Messages |  | 0.612327 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 90 |  | L80X8 |  | Beam |  | No Messages |  | 0.613299 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 91 |  | L80X8 |  | Beam |  | No Messages |  | 0.613299 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 92 |  | L80X8 |  | Beam |  | No Messages |  | 0.612327 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 93 |  | L80X8 |  | Beam |  | No Messages |  | 0.610398 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 94 |  | L80X8 |  | Beam |  | No Messages |  | 0.607547 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 95 |  | L80X8 |  | Beam |  | No Messages |  | 0.603794 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 96 |  | L80X8 |  | Beam |  | No Messages |  | 0.599821 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 97 |  | L80X8 |  | Beam |  | No Messages |  | 0.59631 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 98 |  | L80X8 |  | Beam |  | No Messages |  | 0.593291 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 99 |  | L80X8 |  | Beam |  | No Messages |  | 0.590814 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 100 |  | L80X8 |  | Beam |  | No Messages |  | 0.588918 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 101 |  | L80X8 |  | Beam |  | No Messages |  | 0.587636 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 102 |  | L80X8 |  | Beam |  | No Messages |  | 0.586989 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 103 |  | L80X8 |  | Beam |  | No Messages |  | 0.586989 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |
| 104 |  | L80X8 |  | Beam |  | No Messages |  | 0.587636 | PMM | UDSTL10 | 0.42465 | No Messages |  | No Messages |

Deflection Control

For Dead + Live case the deflection must be <=L/240 (UBC-97, Table16-D) so Maximum

deflection is equal to 22 mm (5500/240=22 mm). With sap analysis maximum

deflection 13 millimeter was obtained for DEFLECTION load case (DEAD + LIVE).

Main Rafter Design Example:

Lateral Beam Design Example: