## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-QC-PR-0006_V01 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0015 |  |  | Transmital Date: 2025/02/26
Document Title: MECHANICAL RUNNING TEST PROCEDURE |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0309-QC-TR-KP-0015 |  |  | Transmital Date:
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-KP-120-QC-PR-0006_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | list of standards and edition shall be added ISO 9906 |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 | N/A. |  |  | It is applicable for diesel pumps for calculating of efficeney of deisel pump pacakge during mechanical running test however,the efficency of package will be measured by performance test procedure. So it is also necessary to be added in this document. vendor reply: It is not applicable for diesel pump. We use iso10816.
2 | relevant table to Clause 8.1.4.1 shall be added |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 | Confirm. |  |  | Noted
3 | vendor to clarify based on which standard Vibration test and sound level test for diesel pump is not applicable |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 | According to diesel is not made of Kalaye pump and diesel with pump are a same skid, measuring pump vibration and sound N/A. but we can refer to iso10816 ,table A1 for diesel vibration. And refer to diesel spec. for diesel sound. |  |  | Kalay pump is reposible of whole package, so vendor can supply a diesel which can meet the standard requirment. vendor reply: its revised.
4 | mentioned below point: Test fluid is clean water at the temperature less than 40ºC. The following meters can be used for testing:Electromagnetic or orifice or venture flow meter, optical temperature meter, digital photo- optical speed counter, vibration measuring meter in mm/s RMS unit, phonometer for noise level. Unless otherwise specified, seal specified in contract shall be used in pump for testing. 4 hours mechanical running test, with job motor if power is right for water. Test items are: 1- Vibration of pump and electromotor bearing at Horizontal & Vertical & Axial direction. 2- Temperature of pump and electromotor bearing. 3- Speed of pump shaft. 4- Noise level at 1meter distance around of package. 5- leakage by visual checking from mechanical seal running test shall be done under the rated flow (if power is right for water), running for 4 hours and the above items shall be recorded ever 1 hours. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 | All this items is mentioned. |  |  | Noted, but the document have revised based on these items, please reflect all of these criteria in your documents and revision mark shall be considered. vendor reply: added.
| any where that used of "if any" and "unless otherwise specified" shall be deleted |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 |  |  |  | vendor to remove only the condition "if specified" or "Unless Other wise", not whole sentences. vendor reply: deleted.
V01
1 | Previous comment 1,4,5 are still vaild, it shall be applied in next revision, if you need more clarification add to comment in this list |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | Confirm.
2 | Debby is a persian word,please remove it from english context |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | if any ,Confirm.
3 | please remove (if any) from clause 8.1.2 |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | Confirm.
4 | Vedor just mentioned Noise of "pump set", so it shall be revised and mentioned in table based on TAG, electro pump, jocky pumps and diesel pumps and limited Noise level shall be sepecified for each items. |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | Confirm.
5 | Critera for Measing temp and limited shall be added in the procedure |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | Its mentioned. Please clarify.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date:1/19/2025 |  |  |  |  | Date: