## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-QC-PR-0007_V01 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0015 |  |  | Transmital Date: 2025/02/26
Document Title: PERFORMANCE TEST PROCEDURE |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0309-QC-TR-KP-0015 |  |  | Transmital Date: 2025/02/26
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-KP-120-QC-PR-0007_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Find attached file. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 | به نحو مقتضی اعمال گردید. |  |  | Not acceptable
V01
| Pursuant to your reply in the document, please be informed that these pumps are based on API610 and NFPA 20, so these standards have already referred in API 610, For instance : ISO 9906 Grade 1: Clause 8.3.1.2: This clause states that performance and NPSH (Net Positive Suction Head) tests should be conducted using methods and uncertainty requirements of ISO 9906 Grade 1, ANSI/HI 1.6 (for centrifugal pumps), or ANSI/HI 2.6 (for vertical pumps). |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A. NPSH test not included in P.O.
| if you consider above comment, ISO9906 shall be followed as per API610, so, in this ISO 9906 , the below standards are referred: SO 9906:2012 references the following standards: ISO 5167-1: Referenced in Clause D.3.2, which discusses the measurement of flow rate using pressure differential devices such as orifice plates, nozzles, and Venturi tubes. ISO 1438-1: Referenced in Clause D.3.5, pertaining to the measurement of liquid flow in open channels using thin-plate weirs. ISO 9104: Referenced in Clause D.3.7, related to the use of electromagnetic flow meters for measuring the volumetric flow rate of electrically conductive liquids. These references can be found in Annex D of ISO 9906:2012, which provides guidance on various flow measurement methods applicable during pump testing. So previous comments shall be applied and it is not related to list of standard in project documents |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
| ISO 5167-1:2022 (Flow measurement with pressure differential devices): Clause D.3.2: This clause in Annex D discusses the use of ISO 5167-1 for measuring flow using pressure differential devices (such as orifice plates, Venturi tubes, and nozzles). It explains the standard's applicability when conducting flow rate measurements during pump testing. ISO 1438-1:1980 (Flow measurement in open channels using thin-plate weirs): Clause D.3.5: This section references ISO 1438-1 in relation to flow measurement methods using thin-plate weirs, which can be used in open channel flow measurements during pump testing. ISO 9104:1991 (Electromagnetic flow meters for liquid flow): Clause D.3.7: ISO 9104 is cited here for the use of electromagnetic flow meters when measuring the volumetric flow rate of electrically conductive liquids in closed conduits during pump performance testing. |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
| ISO 3744:2010 and ISO 3746:2010 are referenced in API 610. Specifically, ISO 3744:2010 is cited in Clause 4.2.9 of API 610,ISO 3746:2010 is also referenced in Clause 4.2.9 ISO 3744:2010 specifies methods for determining the sound power level or sound energy level of a noise source from sound pressure levels measured on a surface. ISO ISO 3746:2010 specifies methods for determining the sound power levels and sound energy levels of noise sources using sound pressure, employing a survey method with an enveloping measurement surface over a reflecting plane. |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
| NPSH test is also part of your scope of work, so vendor is requested to added NPSH test section or issue the relevant procedure.Also see clause 9.1 of ITP |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date:1/19/2025 |  |  |  |  | Date: