## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-QC-PR-0009_V01 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0015 |  |  | Transmital Date:2025/02/26
Document Title: SAT PROCEDURE |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0309-QC-TR-KP-0015 |  |  | Transmital Date:2025/02/26
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-KP-120-QC-PR-0009_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Find attached file. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-10 | به نحو مقتضی اعمال گردید. |  |  | Not acceptanle all the comments shall be followed
V01
1 | Pursuant to your clarification, be informed that client has purchased Fire water Pump package which consists of jocky, main electrical and diesel pumps, so all of these pumps shall work suitably with each other during site acceptanace test and follow the NFPA 20 criteria, so vendor is reposble to follow the the string test at Site acceptance. |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
2 | string test is part of SAT procedure |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
3 | In this procedure shall be clearly explained the start-up of each pump and all the set points shall be mentioned and the sequence of startup of each pump shall be clearly mentioned. |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
4 | SAT report table based on TAG number shall be added and in each table the below information shall be added as min: Visual check after transportation and installation Check of electrical and piping connections Uncoupling for no load run Check of rotation 30min no load run Recoupling and alignment check Full load run till stabilization of bearing temp. Check of pump and motor during test run (temperature, vibration, current) Check of pump performance (head, flow) Check of control panel (visualization and settings) Setting of recirculation valve (if any) Simulation of remote control and alarm signal |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | N/A.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date:1/19/2025 |  |  |  |  | Date: