## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-ME-DS-0001 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0002 |  |  | Transmital Date: 2025/02/08
Document Title: DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER MAIN DIESEL PUMP |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0308-ME-TR-KP-0002 |  |  | Transmital Date:
[5 empty] | CRS No: NISOC-CRS-BK-HD-PEDCO-SVTR-KP-0001_V00 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 |  |  | 02/2294/392451 | 1403/10/01 | - پمپ های آتشنشانی مطابق با استاندارد NFPA20 پس از راه اندازی خودکار در زمان حریق تنها توسط اپراتور و به صورت دستی خاموش می گردند لذا تمامی پمپ های آتشنشانی مطابق با استاندارد NFPA20 مجهز به CRV(Circulation relief valve) می باشند بنابراین میزان Minimum flow پمپ های آتشنشانی برابر میزان دبی شیر CRV و برابر 15 m3/h می باشد. پمپ های آتشنشانی، قابلیت کارکرد در شرایط مذکور مطابق با استاندارد NFPA20 را دارا می باشند. - حداکثر توان مصرفی پمپ های آتشنشانی برابر 241 kw می باشد و الکتروموتور براساس استاندارد NFPA20 بدون در نظر گرفتن ضرایب تصحیح می بایست انتخاب گردد. الکتروموتور براساس دما و ارتفاع سایت توسط سازنده الکتروموتور طراحی می گردد بصورتی که توان خروجی الکتروموتور در سایت 250 kw خواهد بود لذا انتخاب الکتروموتور با توان بالاتر مورد نیاز نمی باشد. لازم به توضیح است الکتروپمپ آتشنشانی با ظرفیت مشابه در پروژه گوره – جاسک تست و تحویل شده است.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date:11/27/2024 |  |  |  |  | Date: