## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-ME-DS-0002 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0016 |  |  | Transmital Date: 2025/02/08
Document Title: DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER MAIN ELECTRICAL PUMP |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0308-ME-TR-KP-0016 |  |  | Transmital Date:
[5 empty] | CRS No: PEDCO-CRS- BK-GCS-KP-120-ME-DS-0002_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
V00
1 | set point of pressure sensing line shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Please refer to P&ID |  |  | P&ID is not recived
2 | allowable leakage of packing shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Please refer to O&M |  |  | closed
3 | Hirgan shall specified site condition |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Noted |  |  | closed
4 | Ns and Nss limitation shall be specified @ Qbep of max impller diameter |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Confirmed NSS(m3/h,m,rpm)=8498 NS (rpm, m3/h,m)=867 Speed(rpm):1490 |  |  | accordance to API 610,Q shall be expressed in m3/s
5 | motor manufacturer shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | OME |  |  | closed
6 | In according to Note 21, Flow shall be considered at least 150% of Rated flow, so calculated Nameplate power is not sufficient |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Motor power is sufficient as per attached calculation sheet. (Derating factors such as temperature, elevation will be considered by motor manufacturer.) |  |  | closed
7 | Recheck Nss or clarify how did you reach to it? |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | NSS & NS Calculation based on Qbep of max impeller diameter Q(m3/h):560/2=280 H(m):120 NPSHr(m):4.2 Speed(rpm):1490 |  |  | accordance to API 610,Q shall be expressed in m3/s
8 | by considering of material is it correct to use RF? |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Confirmed |  |  | open.Based on which standard is it designed?ASME B16.1 or ASME B16.5
9 | Gr. 60-40-15 is not correct.it shall be corrected. |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | GGG40(A536 60-40-18) |  |  | closed
10 | case wear ring to be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Bronze(C95200) |  |  | closed
11 | according to API 610 ; MAWP shall be at least 20 barg |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | MAWP is 15 bar (according to NFPA20) |  |  | closed
12 | Baseplate construction shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | PARTIAL TOP DECKING |  |  | closed
13 | Min/Max continues stable flow shall be shown on curve. |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Min continues stable flow is 15 m3/h Max continues stable flow is 681.3 m3/h |  |  | open.refer to row 32
14 | Efficiency curve shall be added |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | It is not possible |  |  | open,refer to row 33
15 | NPSHR Curve startig point shall be revised vendor shall clarify why start it from 0? |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Fire water pump should be capable to work in shut of point. |  |  | Not acceptable.refer to row 34
V01
1 | Repeated comments : set point of pressure sensing line shall be specified |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC: Set point of pressure sensing line will be done during precommisioning.
2 | Repeated comments : allowable leakage of packing shall be specified |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC: Allowable leakage of packing will be done during precommisioning.
3 | Repeated comments : Starting method shall be mentioned Open Valve in Data sheet |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC: Confirmed
4 | it seems that 15 m3/h is too low for this pump and not correct.please recheck.Doesn't it cause vibration? |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:15 m3/h is confirmed
5 | why it isn't possible?clarify |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:Efficiency curve will be submitted during performance test.
6 | please clarify how is it possible to draw NPSHR or power curve from 0 ? |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:Fire fighting pumps are designed to operate in any working condition.
7 | some of Confirmed comments are not mentioned in document.so it has not been sent to client and returned to you.it shal be replaced after |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:Noted
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 1/27/2025 |  |  |  |  | Date: