## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-ME-DS-0003 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0016 |  |  | Transmital Date: 2025/02/08
Document Title: DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0308-ME-TR-KP-0016 |  |  | Transmital Date:
[5 empty] | CRS No: PEDCO-CRS- BK-GCS-KP-120-ME-DS-0002_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
V00
1 | Hirgan shall specified site condition |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Noted |  |  | closed
2 | Rated curve BEP Flow shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | 19 m3/h |  |  | closed
3 | Ns and Nss limitation shall be specified @ Qbep of max impller diameter |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | NSS & NS Calculation based on Qbep of max impeller diameter Q(m3/h):23 H(m):128 NPSHr(m):1.7 Speed(rpm):2950 |  |  | accordance to API 610,Q shall be expressed in m3/s
4 | motor manufacturer shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | OME |  |  | closed
5 | in according to API 610, Table 12 it shall be corrected. API Factor for P<22 is 1.25 |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Motor power is sufficient MAX power is 16.8 kw (Derating factors such as temperature, elevation will be considered by motor manufacturer.) |  |  | closed
6 | Recheck Nss or clarify how did you reach to it? |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | NSS & NS Calculation based on Qbep of max impeller diameter Q(m3/h):23 H(m):128 NPSHr(m):1.7 Speed(rpm):2950 |  |  | accordance to API 610,Q shall be expressed in m3/s
7 | by considering of material is it correct to use RF? |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Confirmed |  |  | open.Based on which standard is it designed?ASME B16.1 or ASME B16.5
8 | Gr. 60-40-15 is not correct.it shall be corrected. |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | GGG40(A536 60-40-18) |  |  | closed
9 | case wear ring to be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Bronze(C95200) |  |  | closed
10 | Hydrotest pressure and test temp. shal be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Hydrotest : 22.5 Barg MAWP temp. :AMB Hydrotest Ttemp. : AMB |  |  | closed
11 | Baseplate construction shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | PARTIAL TOP DECKING |  |  | closed
12 | Mechanical seal shall be cartridge type and manufacturer shall be specified |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Confirmed |  |  | Data sheet shall be supplied based on API 682
13 | Min/Max continues stable flow shall be shown on curve. |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Min continues stable flow is 5.7 m3/h Max continues stable flow is 22.8 m3/h |  |  | Closed
14 | Efficiency curve shall be added |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | It is not possible |  |  | open,refer to row 29
15 | NPSHR Curve startig point shall be revised vendor shall clarify why start it from 0? |  | BK-SUR-ENG-MEC-03-09742 | 2024-11-27 | Fire water pump should be capable to work in shut of point. |  |  | Not acceptable.refer to row 30
V01
1 | why it isn't possible?clarify |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:Efficiency curve will be submitted during performance test.
2 | please clarify how is it possible to draw NPSHR or power curve from 0 ? |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:Fire fighting pumps are designed to operate in any working condition.
3 | it has not been sent to client and returned to you.it shal be replaced after revised |  | BK-SUR-ENG-MEC-03-09978 | 2025-01-25 | KPC:Noted
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 1/27/2025 |  |  |  |  | Date: