## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: |  |  |  | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [9 empty] | شماره صفحه: 1 از 10
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  | سریال | نسخه
|  |  |  | BK | GCS | KP | 120 | ME | DS |  | 0003 | V02
طرح نگهداشت و افزایش تولید 27 مخزن
DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS نگهداشت و افزایش تولید میدان نفتی بینک
V02 | APR-2025 | AFC |  |  |  |  | Kalaye Pump |  |  | M.Fakharian |  |  | S.Faramarzpour
V01 | JAN-2025 | AFC |  |  |  |  | Kalaye Pump |  |  | M.Fakharian |  |  | S.Faramarzpour
V00 | Nov-2024 | IFA |  |  |  |  | Kalaye Pump |  |  | M.Fakharian |  |  | M.Sadeghian
Rev. | Date | Purpose of Issue / Status |  |  |  |  | Prepared by: |  |  | Checked by: |  |  | Approved by: |  | CLIENT Approval
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## Record Sheet
NISOC |  |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: |  |  |  |  | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [13 empty] | شماره صفحه: 2 از 10
053-073-9184 |  |  |  |  | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته |  | نوع مدرک | سریال |  | نسخه
[5 empty] | BK |  | GCS |  | KP |  | 120 | ME |  | DS | 0003 |  | V02
REVISION RECORD SHEET
| page | V00 | V01 | V02 |  | V03 |  | V04 |  | V05 |  |  | page |  | V00 | V01 |  | V02 | V03 | V04 | V05
| 1 | X | X | X | [8 empty] | 65
| 2 | X | X | X | [8 empty] | 66
| 3 | X | [10 empty] | 67
| 4 | X | [10 empty] | 68
| 5 | X | X | X | [8 empty] | 69
| 6 | X | X | [9 empty] | 70
| 7 | X | [10 empty] | 71
| 8 | X | X | [9 empty] | 72
| 9 | X | [10 empty] | 73
| 10 | X | [10 empty] | 74
| 11 | [11 empty] | 75
| 12 | [11 empty] | 76
| 13 | [11 empty] | 77
| 14 | [11 empty] | 78
| 15 | [11 empty] | 79
| 16 | [11 empty] | 80
| 17 | [11 empty] | 81
| 18 | [11 empty] | 82
| 19 | [11 empty] | 83
| 20 | [11 empty] | 84
| 21 | [11 empty] | 85
| 22 | [11 empty] | 86
| 23 | [11 empty] | 87
| 24 | [11 empty] | 88
| 25 | [11 empty] | 89
| 26 | [11 empty] | 90
| 27 | [11 empty] | 91
| 28 | [11 empty] | 92
| 29 | [11 empty] | 93
| 30 | [11 empty] | 94
| 31 | [11 empty] | 95
| 32 | [11 empty] | 96
| 33 | [11 empty] | 97
| 34 | [11 empty] | 98
| 35 | [11 empty] | 99
| 36 | [11 empty] | 100
| 37 | [11 empty] | 101
| 38 | [11 empty] | 102
| 39 | [11 empty] | 103
| 40 | [11 empty] | 104
| 41 | [11 empty] | 105
| 42 | [11 empty] | 106
| 43 | [11 empty] | 107
| 44 | [11 empty] | 108
| 45 | [11 empty] | 109
| 46 | [11 empty] | 110
| 47 | [11 empty] | 111
| 48 | [11 empty] | 112
| 49 | [11 empty] | 113
| 50 | [11 empty] | 114
| 51 | [11 empty] | 115
| 52 | [11 empty] | 116
| 53 | [11 empty] | 117
| 54 | [11 empty] | 118
| 55 | [11 empty] | 119
| 56 | [11 empty] | 120
| 57 | [11 empty] | 121
| 58 | [11 empty] | 122
| 59 | [11 empty] | 123
| 60 | [11 empty] | 124
| 61 | [11 empty] | 125
| 62 | [11 empty] | 126
| 63 | [11 empty] | 127
| 64 | [11 empty] | 128

## Notes
NISOC |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: |  |  | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [7 empty] | شماره صفحه: 3 از 10
053-073-9184 |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه
|  |  | BK | GCS | KP | 120 | ME | DS | 0003 | V02
GENERAL NOTES
| 1 | Vendor shall fill in the blanks and return the completed data sheet along with Motor data sheet, "DOC NO.: BK-GCS-PEDCO-120-EL-DT-0008 & 0009 | [9 empty] | KPC : Confirmed
with his proposal.
| 2 | Vendor shall submit ITP (Inspection & Testing Plan) with his proposal. | [9 empty] | KPC : Confirmed
| 3 | Vendor is requested to confirm the material, or propose appropriate alternative. | [9 empty] | KPC : Confirmed
| 4 | For Instrumentation, Project specification 'Specification For Instrument and Control of package Unit System (PU)' Doc. No. | [9 empty] | KPC : Confirmed
BK-GNRAL-PEDCO-000-IN-SP-0004, shall be followed.
| 5 | Mechanical seal data sheet shall fill in by vendor as per API 682, 4th edition. | [9 empty] | KPC : Confirmed
| 6 | NPSH test shall be done & witnessed if the margin of NPSHr & NPSHa is less than 1. | [9 empty] | KPC : Confirmed
| 7 | The Tie-in flanges shall conform to ASME B-16.1. | [9 empty] | KPC : Confirmed
| 8 | Pump drain shall be terminated at skid edge with flange connection and valved. | [9 empty] | KPC : Confirmed
| 9 | Supplier to indicate which minimum flow pumps can achieve. | [9 empty] | KPC : Confirmed
| 10 | Nozzle loads shall be 2 times the loads shown in API 610 11th Edition. | [9 empty] | KPC : Confirmed
| 11 | Electrical motor shall be rated for the end of curve. | [9 empty] | KPC : Confirmed
| 12 | The Suction line size is 2 " and discharge line is 2 ". | [9 empty] | KPC : Confirmed
| 13 | Pump Manufacturer shall supply all instrumentation for mechanical seals as per API 682 4th Edition and project requirements. | [9 empty] | KPC : Confirmed
| 14 | Based on project instrumentation specification, these equipments are classified as Type C. Electro pump shall include a dedicated | [9 empty] | KPC : Based on project instrumentation specification, these equipments are classified as Type A
controller/ starter panel installed on pump skid as per NFPA 20 (2019). Pressure switch and pressure sensing line and its
accessories are in vendor scope of work and supply. As per NFPA 20 dedicated sensing line and control panel for jockey pumps and separated
from main pumps shall be considered by vendor.
| 15 | Welding repair procedures shall be submitted for approval. | [9 empty] | KPC : Confirmed
| 16 | If pump is self venting there is no need for vent . | [9 empty] | KPC : Confirmed
| 17 | For information on site conditions refer to Process Basis of Design document; Doc.No: BK-GNRAL-PEDCO-000-PR-DB-0001., electrical motor shall be rated | [9 empty] | KPC : Confirmed
according to project site condition. any required protection for pumps in this regard shall be considered by pump manufacturer.
| 18 | Ultrasonic Test shall be performed for forged shaft. | [9 empty] | KPC : Confirmed
| 19 | Couplings shall be dry, flexible and spacer type. | [9 empty] | KPC : Confirmed
| 20 | For electrical motor descriptions, refer to 'Specification For LV Induction Motors' Doc. No. BK-GNRAL-PEDCO-000-EL-SP-0010. | [9 empty] | KPC : Confirmed
| 21 | A local control panel shall be considered by vendor to be located next to the pumps as per "Specification For Fire Water Pumps", Doc. No. BK-GCS-PEDCO-120-ME-SP-0005'. | [9 empty] | KPC : Confirmed
Network", Doc.No.BK-GCS-PEDCO-120-SA-PI-0001. Pump LCP shall be designed to manage all required monitoring and control signals ,
as minimum in accordance with "P&ID For Fire Water Network", Doc.No.BK-GCS-PEDCO-120-SA-PI-0001.
| 22 | Pressure sensing lines are in the vendor's scope of supply. | [9 empty] | KPC : Confirmed
| 23 | For technical requirements of electrical lv motors refer to "Data sheets "for lv induction motors: DOC NO:BK-GCS-PEDCO-120-EL-DT-0008". | [9 empty] | KPC : Confirmed
Power Factor, efficeincy, frequent, voltage, frequent variation and voltage variation of motor shall be specified by vendor in data sheet.

## P-2302 A,B (1)
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: | [5 empty] | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [12 empty] | شماره صفحه: 4 از 10
053-073-9184 | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
[6 empty] | BK |  | GCS |  | KP |  | 120 | ME | DS | 0003 |  | V02
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2302 A/B (Sheet 1 of 6)
[9 empty] | CLIENT: |  | National Iranian South Oil Company (NISOC)
[9 empty] | PROJECT TITLE: |  | BINAK Gas Compressor Station
JOB NUMBER:
[9 empty] | EQUIPMENT NUMBER: |  | P-2302 A/B
[9 empty] | EQUIPMENT SERVICE: |  | Fire Water Jockey Pumps
SERIAL NUMBER:
[9 empty] | REQ. / SPEC NO. : |  | BK-GCS-PEDCO-120-ME-SP-0005
PURCH ORDER NO.
|  | Cells coloured thus |  |  |  |  | contain drop-down options
contain calculated values based on input data; do not change.
identify a cross referenced paragraph in the document note, and may also contain a drop down list
When you have completed the DS, highlight the whole page format cells pattern none
Delete these notes on completion
COMMENTS:
DATA SHEETS
|  |  |  | ITEM No. |  |  |  |  | ATT |  | ITEM No. |  |  |  |  | ATT |  | ITEM No. |  | ATT
| PUMP |  |  | P-2302 A |  |  |  |  | YES |  | P-2302 B |  |  |  |  | YES
MOTOR
GEAR
TURBINE

## P-2302 A,B (2)
NISOC | [10 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: | [10 empty] | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [17 empty] | شماره صفحه: 5 از 10
053-073-9184 | [10 empty] | پروژه |  | بسته کاری |  | صادرکننده |  | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
[11 empty] | BK |  | GCS |  | KP |  | 120 |  | ME |  | DS |  | 0003 |  |  | V02
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2302 A/B (Sheet 2 of 6)
APPLICABLE TO: |  |  |  |  | PROPOSAL | [13 empty] | APPLICABLE NTL/INTNTL STANDARD: | [7 empty] | NFPA20 (2019) & IPS-M-PM-125
FOR |  |  | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC | NISOC |  | UNIT
SITE |  |  | BINAK Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station | MANSOURI Gas Compressor Station |  | SERVICE |  |  | Fire Water Jockey Pumps
NO. REQ |  |  | 2 (1+1) | [5 empty] | PUMP SIZE |  |  |  | 2 "x 1" | [5 empty] | TYPE |  |  | OH2 (V.T.A) |  |  |  |  | No. STAGES |  |  |  | 1
MANUFACTURER | [11 empty] | KALAYE PUMP CO. | [6 empty] | MODEL |  |  | V.T.A. |  | KP2532 |  |  | SERIAL NO. |  |  |  | V.T.A.
LIQUID CHARACTERISTICS
[8 empty] | Units |  |  | Maximum |  |  | Minimum |  |  | Note |  |  | SERVICE : | [10 empty] | INTERMITTENT
LIQUID TYPE OR NAME : | [7 empty] | Water | [8 empty] | Max & min |  |  | • IF INTERMITTENT NO. OF STARTS :
VAPOR PRESSURE : | [7 empty] | bara |  |  | 0.0087 |  |  | 0.1219 |  |  | values refer |  |  | PUMPS OPERATE IN:
DENSITY : | [7 empty] | kg/m³ |  |  | 997 | [5 empty] | only to the |  |  | CORROSION DUE TO : (6.12.1.9)
SPECIFIC HEAT : | [7 empty] | kj/kgC |  |  | 4.186 |  |  | 4.186 |  |  | property |  |  | EROSION DUE TO : (6.12.1.9)
VISCOSITY : | [7 empty] | cP |  |  | 1 | [5 empty] | listed |  |  | H2S CONCENTRATION (ppm) : (6.12.1.12) | [12 empty] | N.A.
OPERATING CONDITIONS (6.1.2) | [19 empty] | CHLORIDE CONCENTRATION (ppm) :
[8 empty] | Units |  |  | Maximum |  |  | Rated |  | Normal |  | Min |  | PARTICULATE SIZE (DIA IN MICRONS)
NPSHA Datum: | [10 empty] | C.L. Impeller | [8 empty] | PARTICULATE CONCENTRATION (PPM)
PUMPING TEMPERATURE : | [7 empty] | oC |  |  | 50 | [6 empty] | 5
FLOW : | [7 empty] | m3/hr | [5 empty] | 15
DISCHARGE PRESSURE :(6.3.2) | [7 empty] | barg | [5 empty] | 10.4
SUCTION PRESSURE : | [7 empty] | barg |  |  | 0.83 |  |  | 0.81 |  |  |  | 0.08
DIFFERENTIAL PRESSURE : | [7 empty] | bar | [5 empty] | 10.3
DIFFERENTIAL HEAD : | [7 empty] | m | [5 empty] | 105
NPSHA : | [7 empty] | m | [5 empty] | 8.8
HYDRAULIC POWER: | [7 empty] | KW | [5 empty] | 4.5
SITE AND UTILITY DATA
LOCATION: | [19 empty] | COOLING WATER :
|  | OUTDOOR |  |  |  |  | UNHEATED |  |  |  |  | UNDER ROOF | [14 empty] | RETURN |  |  | DESIGN
MOUNTED AT : | [10 empty] | l | TROPICALISATION REQ'D | [8 empty] | TEMP |  |  |  |  | MAX
ELECTRIC AREA CLASSIFICATION: | [9 empty] | (6.1.22) |  |  | ZONE |  | SAFE | [5 empty] | PRESS. |  |  |  |  | MIN
GROUP | [10 empty] | TEMP CLASS | [9 empty] | SOURCE
SITE DATA : | [20 empty] | COOLING WATER CHLORIDE CONCENTRATION: | [11 empty] | ppm
ELEVATION (MSL) : | [5 empty] | 12.5 |  | m |  |  |  | BAROMETER : |  |  |  | 990.77 |  | mBar |  | INSTRUMENT AIR : | [7 empty] | kg |  | MIN |  |  | kg
RANGE OF DESIGN TEMPS:MIN / MAX | [10 empty] | 5 |  |  | 85 |  | oC |  |  |  | STEAM
RELATIVE HUMIDITY: MIN / MAX | [10 empty] | 0 |  |  | 100 |  | % | (@ 25.6 oC) | [7 empty] | DRIVERS |  |  | HEATING
UNUSUAL CONDITIONS: | [10 empty] | NA | [9 empty] | TEMP
UTILITY CONDITIONS : | [20 empty] | PRESS. |  | kg
ELECTRICITY : |  |  |  |  | DRIVERS |  |  | HEATING |  |  | CONTROL |  |  | SHUTDOWN
| VOLTAGE |  |  |  | 400
| PHASE |  |  |  | 3
| HERTZ |  |  |  | 50
PERFORMANCE | [19 empty] | DRIVER (7.1.5) (NOTES 11,20,17)
PROPOSAL CURVE NO. | [6 empty] | KP 2532 |  |  |  |  | RPM |  | 2950 | [5 empty] | Driver Type | [8 empty] | INDUCTION MOTOR
| As Tested Curve No. | [12 empty] | KP 2532 | [5 empty] | GEAR | [11 empty] | NO
IMPELLER DIA.: |  |  |  | RATED |  | 286 |  | MAX. |  | 324 |  | MIN. |  | 250 |  | mm |  |  |  | VARIABLE SPEED REQUIRED | [11 empty] | NO
RATED POWER |  |  |  |  | 14.8 |  | Kw |  |  | EFFICIENCY |  |  |  | 29 |  | (%) |  |  |  | SOURCE OF VARIABLE SPEED
RATED CURVE BEP FLOW (at rated impeller dia) | [13 empty] | 19 |  | m³/hr |  |  |  | OTHER
MIN FLOW : |  |  |  | THERMAL | [7 empty] | STABLE |  | 5.7 |  | m³/hr |  |  |  | MANUFACTURER | [10 empty] | OME
PREFERRED OPERATING REGION (6.1.11) | [10 empty] | 13.3 |  | to | 22.8 |  | m³/hr |  |  |  | NAMEPLATE POWER | [5 empty] | @Site Condition |  |  | 18.5 |  |  |  |  | KW
ALLOWABLE OPERATING REGION | [10 empty] | 5.7 |  | to | 22.8 |  | m³/hr |  |  |  | Nominal RPM | [8 empty] | 2950
MAX HEAD @ RATED IMPELLER | [13 empty] | 119 |  | m |  |  |  | RATED LOAD RPM
MAX POWER @ RATED IMPELLER | [13 empty] | 16.8 |  | kW |  |  |  | FRAME OR MODEL
NPSH3 AT RATED FLOW : | [13 empty] | 1.5 |  | m |  |  |  | ORIENTATION | [8 empty] | HORIZONTAL
CL PUMP TO U/S BASEPLATE | [15 empty] | m |  |  |  | LUBE | [8 empty] | Grease
NPSH MARGIN AT RATED FLOW : | [13 empty] | 7.3 |  | m |  |  |  | BEARING TYPE:
SPECIFIC SPEED (6.1.9) | [19 empty] | RADIAL | [8 empty] | Ball / 1
SUCTION SPECIFIC SPEED LIMIT | [13 empty] | 372 | [5 empty] | THRUST | [8 empty] | Ball / 1
SUCTION SPECIFIC SPEED | [13 empty] | 9502 | [5 empty] | STARTING METHOD | [6 empty] | D.O.L /Open delivery valve
MAX. ALLOW. SOUND PRESS. LEVEL REQD (6.1.14) | [13 empty] | 85 |  | (dBA) |  | @ 1 m |  | SEE DRIVER DATA SHEET | [10 empty] | Note 1
EST MAX SOUND PRESS. LEVEL | [13 empty] | 85 |  | (dBA) |  |  |  | Max Voltage Variation | [10 empty] | Acc. to "Motor D.Sh. For Fire Water Main Jockey Pumps (BK-GCS-KP-120-EL-DS-0002)
MAX. SOUND POWER LEVEL REQ'D (6.1.14) | [19 empty] | Max Frequency Variation
EST MAX SOUND POWER LEVEL | [19 empty] | Max Voltage and Frequency Variation together

## P-2302 A,B (3)
NISOC | [8 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: | [8 empty] | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [16 empty] | شماره صفحه: 6 از 10
053-073-9184 | [8 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  |  | نسخه
[9 empty] | BK |  | GCS |  | KP | 120 |  | ME |  | DS |  | 0003 |  |  | V02
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2302 A/B (Sheet 3 of 6)
CONSTRUCTION
API PUMP TYPE: |  |  |  | OH2 |  | [Based on API 610 definitions] | [10 empty] | CASING MOUNTING: | [9 empty] | CENTERLINE
[17 empty] | CASING TYPE: | [5 empty] | (6.3.10) |  |  |  | SINGLE VOLUTE
NOZZLE CONNECTIONS: | [5 empty] | (6.5.5) |  |  | NOTES 7, 12 | [7 empty] | OH3 BACKPULLOUT LIFTING DEVICE REQD. (9.1.2.6)
[5 empty] | Size |  | Facing |  | Rating |  |  | Position | [5 empty] | CASE PRESSURE RATING:
SUCTION |  |  |  |  | 2" |  | RF |  | 300 |  |  | END | [7 empty] | MAWP : | MAWP : |  | (6.3.5) |  | 15 | By vendor |  |  |  | barg | @ | Amb. |  |  |  | oC
DISCHARGE |  |  |  |  | 1" |  | RF |  | 300 |  |  | TOP | [7 empty] | HYDROTEST : |  |  |  |  | 22.5 | 1.5*MAWP |  |  |  | barg | @ | Amb. |  |  |  | oC
PRESSURE CASING AUX. CONNECTIONS: (6.4.3.2)
|  |  | No. |  | Size |  | Type |  | Facing |  | Rating |  | Posn. |  |  |  |  | HYDROTEST OH PUMP AS ASSEMBLY | [14 empty] | YES
BAL./LEAK OFF | [17 empty] | SUCT'N PRESS. REGIONS DESIGNED FOR MAWP | [14 empty] | YES
DRAIN |  |  | 1 |  | 1/2" |  | SWF |  | RF |  | 150 |  | SIDE |  |  |  |  | ROTATION: |  |  |  | (VIEWED FROM COUPLING END) | [10 empty] | CW
VENT | [18 empty] | • | IMPELLERS INDIVIDUALLY SECURED : | [11 empty] | YES
PRESSURE GAGE | [18 empty] | • | BOLT OH 3/4/5 PUMP TO PAD / FOUNDATION :
TEMP GAGE | [18 empty] | • | PROVIDE SOLEPLATE FOR OH 3/4/5 PUMPS
WARM-UP LINE | [17 empty] | ROTOR:
SHAFT FLEXIBILITY INDEX (SFI) (9.1.1.3)
| Drain Valve Supplied By | [9 empty] | SUPPLIER | [6 empty] | First Critical Speed Wet (Multi stage pumps only)
| DRAINS MANIFOLDED | [9 empty] | YES | [6 empty] | COMPONENT BALANCE TO ISO 1940 G1.0 | [14 empty] | NO
| VENT Valve Supplied By | [9 empty] | SUPPLIER | [6 empty] | SHRINK FIT -LIMITED MOVEMENT IMPELLERS (9.2.2.3)
| VENTS MANIFOLDED | [9 empty] | YES | [6 empty] | COUPLING:(7.2.3) | [5 empty] | (7.2.13.f) |  |  |  | NOTE 16
| THREAD. CONS FOR PIPELINE SERVICE & < 50°C (6.4.3.2) | [11 empty] | NO |  |  |  |  | MANUFACTURER | [10 empty] | Colossus
| SPECIAL FITTINGS FOR TRANSITIONING (6.4.3.3) | [11 empty] | NO |  |  |  |  | MODEL | [10 empty] | FLEXIBLE SPACER TYPE
| CYLINDRICAL THREADS REQUIRED (6.4.3.8) | [11 empty] | NO |  |  |  |  | RATING (POWER/100 RPM)
| GUSSET SUPPORT REQUIRED | [11 empty] | YES |  | If Needed |  |  | SPACER LENGTH | [14 empty] | 140 |  | mm
| MACHINED AND STUDDED CONNECTIONS (6.4.3.12) | [11 empty] | NO |  |  |  |  | SERVICE FACTOR | [14 empty] | Min 1.5
| VS 6 DRAIN | [9 empty] | N/A | [6 empty] | RIGID | [14 empty] | NO
| DRAIN TO SKID EDGE | [11 empty] | YES |  |  |  |  | COUPLING WITH HYDRAULIC FIT (7.2.10)
MATERIAL (6.12.1.1) | [17 empty] | COUPLING BALANCED TO ISO 1940-1 G6.3 (7.2.3) | [14 empty] | YES
APPENDIX H CLASS | [7 empty] | I-2 |  |  | NOTE 3 | [6 empty] | COUPLING WITH PROPRIETARY CLAMPING DEVICE (7.2.11)
MIN DESIGN METAL TEMP (6.12.4.1) | [11 empty] | 5 |  |  | °C
REDUCED-HARDNESS MATERIALS REQ'D (6.12.1.12.1) | [17 empty] | COUPLING IN COMPLIANCE WITH (7.2.4) | [11 empty] | API 671
Applicable Hardness Standard (6.12.1.12.3) | [17 empty] | COUPLING GUARD STANDARD PER (7.2.13.a) | [12 empty] | ISO 14120
BARREL : | [17 empty] | Window on Coupling Guard | [14 empty] | YES
CASE : | [7 empty] | GGG40(A536 60-40-18)
DIFFUSERS | [16 empty] | BASEPLATE
IMPELLER : | [7 empty] | C95200 | [9 empty] | API BASEPLATE NUMBER :
IMPELLER WEAR RING : | [7 empty] | C95200 | [9 empty] | BASEPLATE CONSTRUCTION (7.3.14) | [9 empty] | PARTIAL TOP DECKING
CASE WEAR RING : | [7 empty] | C95200 | [9 empty] | BASEPLATE DRAINAGE (7.3.1) | [9 empty] | Entire Baseplate Drain Pan
SHAFT: | [7 empty] | A276 T420 | [9 empty] | MOUNTING :
Bowl (if VS-type) | [17 empty] | NON-GROUT CONSTRUCTION : (7.3.13)
Inspection Class (Note 2) | [17 empty] | VERTICAL LEVELING SCREWS : | [9 empty] | REQUIRED
BEARINGS AND LUBRICATION (6.10.1.1) (VTC) | [17 empty] | LONGITUDINAL DRIVER POSITIONING SCREWS : | [12 empty] | REQUIRED
BEARING (TYPE / NUMBER): | [5 empty] | (6.11.4) | [11 empty] | SUPPLIED WITH : |  |  |  |  | l | GROUT AND VENT HOLES | [9 empty] | YES
| RADIAL | ROLLER |  |  |  |  | / |  | 1 | [13 empty] | l | DRAIN CONNECTION | [9 empty] | YES
| THRUST | BALL |  |  |  |  | / |  | 2 | [8 empty] | MOUNTING PADS SIZED FOR BASEPLATE LEVELING (7.3.5) | [15 empty] | YES
REVIEW AND APPROVE THRUST BEARING SIZE : (9.2.5.2.4) | [17 empty] | MOUNTING PADS TO BE MACHINED (7.3.6) | [15 empty] | YES
[18 empty] | PROVIDE SPACER PLATE UNDER ALL EQUIPMENT FEET | [15 empty] | YES
LUBRICATION : |  |  | (6.10.2.2) (6.11.3) (9.2.6) | [6 empty] | RING OIL | [7 empty] | OTHER
| PRESSURE LUBE SYSTEM TO ISO 10438- | [9 empty] | (9.2.6.5)
ISO 10438 DATA SHEETS ATTACHED
| Pressurized Lube Oil System mtd on pump baseplate | [16 empty] | REMARKS :
Location of Pressurized Lube Oil System mounted on baseplate :
| INTERCONNECTING PIPING PROVIDED BY | [9 empty] | Supplier
| OIL VISC. ISO GRADE | [8 empty] | VG
CONSTANT LEVEL OILER :

## P-2302 A,B (4)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: |  |  |  | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [11 empty] | شماره صفحه: 7 از 10
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
|  |  |  | BK | GCS | KP | 120 | ME |  | DS |  | 0003 |  | V02
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2302 A/B (Sheet 4 of 6)
INSTRUMENTATION | [8 empty] | SEAL SUPPORT SYSTEM MOUNTING
SEE ATTACHED API-670 DATA SHEET | [9 empty] | SEAL SUPPORT SYSTEM MOUNTED ON PUMP BASEPLATE
ACCELEROMETER (7.4.2.1) | [16 empty] | (7.5.1.4) |  |  | YES
| Number of Accelerometers | [8 empty] | IDENTIFY LOCATION ON BASEPLATE
Mounting Location of Accelerometers
[10 empty] | INTERCONNECTING PIPING BY | [7 empty] | Supplier
| PROVISION FOR MTG ONLY |  | (6.10.2.10)
| Number of Accelerometers | [7 empty] | MECHANICAL SEAL (6.8.1) (NOTE 13)
| Mounting Location of Accelerometers | [8 empty] | SEE ATTACHED ISO 21049/API 682 DATA SHEET | [9 empty] | N / A | NOTE 5
[10 empty] | ADDITIONAL CENTRAL FLUSH PORT | [6 empty] | (6.8.9)
| FLAT SURFACE REQUIRED |  | (6.10.2.11) | [6 empty] | HEATING JACKET REQ'D. | [6 empty] | (6.8.11) |  |  | N / A
| Number of Accelerometers | [8 empty] | FLUSH PLAN | [9 empty] | 11+61 | (VTC)
Mounting Location of Accelerometers
VIBRATION PROBES (7.4.2.2) | [8 empty] | HEATING AND COOLING (6.1.17)
| PROVISIONS FOR VIB. PROBES | [8 empty] | COOLING REQ'D | [9 empty] | NO
| NUMBER PER RADIAL BEARING | [8 empty] | COOLING WATER PIPING PLAN
| NUMBER PER AXIAL BEARING | [8 empty] | COOLING WATER PIPING
FITTINGS
| MONITORS AND CABLES SUPPLIED BY (7.4.2.4) | [8 empty] | COOLING WATER PIPING MATERIALS
COOLING WATER REQUIREMENTS:
TEMPERATURE (7.4.2.3) | [18 empty] | BEARING HOUSING
| PROVISIONS FOR TEMP PROBES | [17 empty] | HEAT EXCHANGER
| RADIAL BEARING TEMP. | [8 empty] | TOTAL COOLING WATER
|  | NUMBER PER RADIAL BEARING | [7 empty] | HEATING MEDIUM
| THRUST BEARING TEMP. | [9 empty] | OTHER
|  | NUMBER PER THRUST BEARING ACTIVE SIDE | [7 empty] | HEATING PIPING
NUMBER PER THRUST BEARING INACTIVE SIDE
| TEMP. GAUGES (WITH THERMOWELLS) (9.1.3.6) | [7 empty] | PIPING & APPURTENANCES
| PRESSURE GAUGE TYPE | [8 empty] | MANIFOLD PIPING FOR PURCHASER CONNECTION (7.5.1.6)
| Remarks | [11 empty] | VENT |  |  |  |  | YES
[13 empty] | DRAIN |  |  |  |  | YES
[13 empty] | VALVES |  |  |  |  | YES (NOTE 8)
[13 empty] | COOLING WATER | [6 empty] | NO
[11 empty] | TAG ALL ORIFICES (7.5.2.4) | [8 empty] | YES
SOCKET WELD CONN ON SEAL GLAND (7.5.2.8)

## P-2302 A,B (5)
NISOC | [5 empty] | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: | [5 empty] | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [14 empty] | شماره صفحه: 8 از 10
053-073-9184 | [5 empty] | پروژه |  | بسته کاری |  | صادرکننده | تسهیلات | رشته |  | نوع مدرک |  | سریال |  | نسخه
[6 empty] | BK |  | GCS |  | KP | 120 | ME |  | DS |  | 0003 |  | V02
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2302 A/B (Sheet 5 of 6)
SURFACE PREPARATION AND PAINT | [12 empty] | TEST
MANUFACTURER'S STANDARD | [13 empty] | SHOP INSPECTION (8.1.1) | [10 empty] | Yes
OTHER (SEE BELOW) | [13 empty] | PERFORMANCE CURVE
SPECIFICATION NO. |  |  | BK-GNRAL-PEDCO-000-PI-SP-0006, "Specification | [10 empty] | & DATA APPROVAL PRIOR TO SHIPMENT. | [10 empty] | YES
|  |  | for Painting" | [10 empty] | TEST WITH SUBSTITUTE SEAL (8.3.3.2.b)
PUMP: | [13 empty] | MATERIAL CERTIFICATION REQUIRED | [8 empty] | CASING |  | YES
PUMP SURFACE PREPARATION | [5 empty] | SA 2 1/2 | [7 empty] | SHAFT |  |  | YES |  |  |  | (6.12.1.8) |  | IMPELLER |  | YES
PRIMER |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | OTHER |  |  | YES |  | Casing and impeller Wear ring
FINISH COAT |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | CASTING REPAIR WELD PROCEDURE APPR REQD | [10 empty] | YES
BASEPLATE: | [13 empty] | INSPECTION REQUIRED FOR CONNECTION WELDS (6.12.3.4.d) KPC:NOT APPLICABLE
BASEPLATE SURFACE PREPARATION | [5 empty] | SA 2 1/2 | [7 empty] | LIQUID PENETRANT |  |  |  |  | YES |  |  | MAG PARTICLE
PRIMER: |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | ULTRASONIC | [7 empty] | RADIOGRAPHY |  |  | YES
FINISH COAT |  |  |  |  | AS PER PROJECT PAINTING SPEC. | [8 empty] | INSPECTION REQUIRED FOR CASTINGS
DETAILS OF LIFTING DEVICES | [13 empty] | LIQUID PENETRANT |  |  |  |  | YES |  |  | MAG PARTICLE |  |  | NO
SHIPMENT: (8.4.1) | [7 empty] | EXPORT | [5 empty] | ULTRASONIC (NOTE 18) |  |  |  |  | YES |  |  | RADIOGRAPHY
EXPORT BOXING REQUIRED | [9 empty] | YES |  |  |  | HARDNESS TEST REQUIRED (8.2.2.7)
OUTDOOR STORAGE MORE THAN 6 MONTHS | [9 empty] | YES |  |  |  | ADDNL SUBSURFACE EXAMINATION (6.12.1.5) (8.2.1.3)
SPARE ROTOR ASSEMBLY PACKAGED FOR: | [21 empty] | FOR
ROTOR STORAGE ORIENTATION (9.2.8.2) | [21 empty] | METHOD
SHIPPING & STORAGE CONTAINER FOR VERT STORAGE (9.2.8.3)
N2 PURGE (9.2.8.4) | [13 empty] | PMI TESTING REQUIRED (8.2.2.8)
SPARE PARTS | [14 empty] | COMPONENTS TO BE TESTED
START-UP | [9 empty] | YES |  |  |  | RESIDUAL UNBALANCE TEST (J.4.1.2)
NORMAL MAINTENANCE | [9 empty] | YES |  |  |  | NOTIFICATION OF SUCCESSFUL SHOP | [10 empty] | YES
|  |  |  | WEIGHTS |  | Kg | [7 empty] | PERFORMANCE TEST (8.1.1.c) (8.3.3.5) | [10 empty] | YES
ITEM No |  | PUMP | DRIVER |  | GEAR |  | BASE |  |  | TOTAL |  |  |  | BASEPLATE TEST (7.3.21)
P-2302 A/B |  | 250 | 146 |  | Not applicable |  | 405 |  |  | 809 |  |  |  | HYDROSTATIC | [9 empty] | WIT
HYDROSTATIC TEST OF BOWLS & COLUMN (9.3.13.2)
[14 empty] | PERFORMANCE TEST | [9 empty] | WIT
OTHER PURCHASER REQUIREMENTS | [13 empty] | TEST IN COMPLIANCE WITH (8.3.3.2) | [9 empty] | NFPA 20
| COORDINATION MEETING REQUIRED (10.1.3) | [8 empty] | YES |  |  |  | TEST DATA POINTS TO (8.3.3.3) | [9 empty] | NFPA 20
| MAXIMUM DISCHARGE PRESSURE TO INCLUDE | [12 empty] | TEST TOLERANCES TO (8.3.3.4) | [9 empty] | TABLE 16
[9 empty] | MAX RELATIVE DENSITY |  |  |  |  | NPSH (8.3.4.3.1) (8.3.4.3.4) (NOTE 6) | [9 empty] | WIT
| OPERATION TO TRIP SPEED | [12 empty] | NPSH-1ST STG ONLY (8.3.4.3.2)
| MAX DIA. IMPELLERS AND/OR NO OF STAGES | [8 empty] | YES |  |  |  | NPSH TESTING TO HI 1.6 OR ISO 9906 (8.3.4.3.3)
| CONNECTION DESIGN APPROVAL (9.2.1.4) | [8 empty] | YES |  |  |  | TEST NPSHA LIMITED TO 110% SITE NPSHA (8.3.3.6)
| TORSIONAL ANALYSIS / REPORT (6.9.2.10) | [8 empty] | NO |  |  |  | RETEST ON SEAL LEAKAGE (8.3.3.2.d) | [9 empty] | OBSERVE
| PROGRESS REPORTS | [8 empty] | YES |  |  |  | RETEST REQUIRED AFTER FINAL HEAD ADJ (8.3.3.7.b)
| OUTLINE OF PROC FOR OPTIONAL TESTS (10.2.5) | [12 empty] | COMPLETE UNIT TEST (8.3.4.4.1) | [9 empty] | WIT
| ADDITIONAL DATA REQUIRING 20 YEARS RETENTION (8.2.1.1) | [12 empty] | SOUND LEVEL TEST (8.3.4.5) | [9 empty] | WIT
[10 empty] | YES |  |  |  | CLEANLINESS PRIOR TO FINAL ASSEMBLY (8.2.2.6) | [9 empty] | OBSERVE | OBSERVE
| LATERAL ANALYSIS REQUIRED (9.1.3.4) (9.2.4.1.3) | [8 empty] | NO |  |  |  | LOCATION OF CLEANLINESS INSPECTION
| MODAL ANALYSIS REQUIRED (9.3.9.2) | [12 empty] | NOZZLE LOAD TEST
| DYNAMIC BALANCE ROTOR (6.9.4.4) | [8 empty] | YES |  |  |  | CHECK FOR CO-PLANAR MOUNTING PAD SURFACES
| INSTALLATION LIST IN PROPOSAL (10.2.3.l) | [8 empty] | YES |  |  |  | MECHANICAL RUN TEST UNTIL OIL TEMP STABLE
| VFD STEADY STATE DAMPED RESPONSE ANALYSIS (6.9.2.3) | [8 empty] | NO | NO |  |  | 4 HR. MECH RUN AFTER OIL TEMP STABLE (8.3.4.2.1) | [9 empty] | WIT
| TRANSIENT TORSIONAL RESPONSE |  |  |  |  | (6.9.2.4) |  |  |  | NO |  |  |  | 4 HR. MECH RUN TEST (8.3.4.2.2)
| BEARING LIFE CALCULATIONS REQUIRED (6.10.1.6) | [12 empty] | BRG HSG RESONANCE TEST (8.3.4.7)
| IGNITION HAZARD ASSMT TO EN 13463-1 (7.2.13.e) | [12 empty] | STRUCTURAL RESONANCE TEST (9.3.9.2)
| CASING RETIREMENT THICKNESS DRAWING (10.3.2.3) | [12 empty] | REMOVE / INSPECT HYDRODYNAMIC BEARINGS AFTER TEST
| FLANGES RQD IN PLACE OF SKT WELD UNIONS (7.5.2.8) | [13 empty] | (9.2.7.5)
| INCLUDE PLOTTED VIBRATION SPECTRA (6.9.3.3) | [12 empty] | AUXILIARY EQUIPMENT TEST (8.3.4.6)
| CONNECTION BOLTING (7.5.1.7) | [12 empty] | EQUIPMENT TO BE INCLUDED IN AUXILIARY TESTS
| CADMIUM PLATED BOLTS PROHIBITED | [12 empty] | LOCATION OF AUXILIARY EQUIPMENT TEST
| VENDOR TO KEEP REPAIR AND HT RCDS (8.2.1.1.c) | [12 empty] | IMPACT TEST |  |  | (6.12.4.3) |  |  | PER EN 13445
| VENDOR SUBMIT TEST PROCEDURES (8.3.1.1) | [8 empty] | YES | [9 empty] | PER ASME SECTION VIII
| SUBMIT INSPECTION CHECK LIST (8.1.5) NOTE 2 | [8 empty] | YES |  |  |  | REMOVE CASING AFTER TEST

## P-2302 A,B (6)
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید پکیج پمپ های آب آتشنشانی ایستگاه تقویت فشارگاز بینک (قرارداد BK-HD-GCS-CO-0023_00)
شماره پیمان: |  |  |  | DATA SHEETS (W/PERFORMANCE CURVE) FOR FIRE WATER JOCKEY PUMPS | [9 empty] | شماره صفحه: 9 از 10
053-073-9184 |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه
|  |  |  | BK | GCS | KP | 120 | ME | DS | 0003 |  | V02
CENTRIFUGAL PUMP DATA SHEET (SI UNIT) - P-2302 A/B (Sheet 6 of 6)
PRESSURE VESSEL DESIGN CODE REFERENCES
THESE REFERENCES MUST BE LISTED BY THE MANUFACTURER
CASTING FACTORS USED IN DESIGN ( TABLE 3)
SOURCE OF MATERIAL PROPERTIES
WELDING AND REPAIRS (NOTE 15)
THESE REFERENCES MUST BE LISTED BY THE PURCHASER. (DEFAULT TO TABLE 11 IF NO PURCHASER PREFERENCE IS STATED)
ALTERNATE WELDING CODES AND STANDARDS
| WELDING REQUIREMENT (APPLICABLE CODE OR STANDARD) | [11 empty] | DEFAULT PER TABLE 11
| WELDER/OPERATOR QUALIFICATION | [11 empty] | DEFAULT PER TABLE 11
| WELDING PROCEDURE QUALIFICATION | [11 empty] | DEFAULT PER TABLE 11
| NON-PRESSURE RETAINING STRUCTURAL WELDING SUCH AS BASEPLATES OR SUPPORTS | [11 empty] | DEFAULT PER TABLE 11
| MAGNETIC PARTICLE OR LIQUID PENETRANT EXAMINATION OF PLATE EDGES | [11 empty] | DEFAULT PER TABLE 11
| POSTWELD HEAT TREATMENT | [11 empty] | DEFAULT PER TABLE 11
| POSTWELD HEAT TREATMENT OF CASING FABRICATION WELDS | [11 empty] | DEFAULT PER TABLE 11
MATERIAL INSPECTION
| THESE REFERENCES MUST BE LISTED BY THE PURCHASER | [9 empty] | DEFAULT TO TABLE 14 |  |  |  | YES
ALTERNATIVE MATERIAL INSPECTIONS AND ACCEPTANCE CRITERIA (SEE TABLE 15) (8.2.2.5)
| TYPE OF INSPECTION |  |  | METHOD |  |  |  | FOR FABRICATIONS |  |  |  |  | FOR CASTINGS
RADIOGRAPHY
ULTRASONIC INSPECTION
MAGNETIC PARTICLE INSPECTION
LIQUID PENETRANT INSPECTION
VISUAL INSPECTION (all surfaces)
REMARKS :