## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-KP-120-QC-PR-0005_V01 |  |  |  |  | Vendor Tr. No. : BK-HD-PEDCO-SVTR-KP-0015 |  |  | Transmital Date: 2025/04/23
Document Title: HYDROSTATIC TEST PROCEDURE |  |  |  |  | PEDCO Tr No. : BK-PEDCO-NISOC-0309-QC-TR-KP-0015 |  |  | Transmital Date:
[5 empty] | CRS No: PEDCO-CRS-BK-GCS-KP-120-QC-PR-0005_V01 |  |  | CRS Status: | CM
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | Table of content shall be added |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Confirm. |  |  | Noted
2 | it is mandatory to use trained personnel for tests. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Test is done by QC. |  |  | Noted
3 | Related Data sheets , project specification and PMR shall be added to references and list of standard shall be added |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | data sheet and project spec. will be added.PMR N/A. List of standard is mentioned. |  |  | Noted
4 | Testing steps shall explained completely, from visual test stage to preparation the pump for hydrotest |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | All steps that need to test is mentioned. |  |  | Noted
5 | All pressure-containing parts that to be tested shall be added. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Confirm. |  |  | Noted
6 | Testing Temperature shall be specified |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Confirm. |  |  | Noted
7 | as section shall be added and preparation for test shall be mentioned below items: 1-Prior to testing, the pressure part shall be thoroughly cleaned and free from dirt, debris, slag, oil and grease, etc. Gauge to be accurate to at least 1.6% of Max. range 2-- All gauges shall be calibrated against a standard deadweight tester or a calibrated master gauge prior to using of them. Calibration certificate (which is approved by recognized calibration agency) shall be prepared and available at time of inspection. 3-Pressure part outside shall be dried completely. 4-Calibrated measuring instruments (pressure gauges) shall be provided. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Confirm. |  |  | it shall be added in next revision all the statement same as the comments shall be reflected in document in page 6. Noted * closed
8 | Measuring and testing equipments and its arrangements shall be added and explained about its specifications. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | N/A. |  |  | Noted, Guage specification and ranges shall be mentioned Vendor reply: N/A. These items is mentoined in calibration and present to inspector. Client: Not acceptable, the requirment of hydrotest and devices are different, so it is necessary to be shown here.
9 | explain your procedure in case that test is not succesful |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | After corrections will be retest. |  |  | Which correction? Please explain clearly Vendor reply: Confirm. Client:Noted and closed, it shall be reflected in documents
10 | after testing necessary actions shall be explained |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Its be mentioned. |  |  | Noted, when you are replying the comment, please refer to relevant section, otherwise vendor is resposible to add and put the revision mark. Vendor reply: Confirm. Client:Noted and closed, it shall be reflected in documents
11 | sample test report shall be added. |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Confirm. |  |  | Noted, the criteria shall be cleary mentioned Vendor reply: please clarify. Client: noted
12 | since there is leakage by using packing instead of mechanical seal in main and diesel pumps, posetive displacement pumps shall keep pressure stable on hydrotest pressure . |  | BK-SUR-ENG-QAC-03-09757 | 2024-12-08 | Confirm. |  |  | Noted, the criteria shall be cleary mentioned Vendor Reply: all casing is closed with blind cap. Client : Noted
V01
1 | the remaning items in previous comment sheet shall be reviewed and applied , if vendor need to do any clarification, comment shall be added here and reply to client in this comment sheet. |  | BK-SUR-ENG-QAC-03-09950 | 2025-01-19 | Confirm. |  |  | Noted, some items needs to be revised in document in next revision
V01(RP)
1 | Confirmed comments shall be reflected to documet. |  | BK-SUR-ENG-QAC-03-10131 | 2025-03-12 | Added.
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: Ah.Behbahani | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 3/9/2025 |  |  |  |  | Date: