## Sheet1
N.I.S.O.C |  | Binak Project
COMMENT REPLY SHEET
Document No: BK-GCS-MF-120-PR-PF-0001 |  |  |  |  | Vendor Tr. N0: BK-HD-PEDCO-SVTR-MF-0004 |  |  | Transmital Date: 2024/03/02
Document Title: PROCESS FLOW DIAGRAM FOR GAS DEHYDRATION PACKAGE |  |  |  |  | Client Tr. No: |  |  | Transmital Date:
[5 empty] | CRS No:PECO- CRS-BK-GCS-MF-120-PR-PF-0001-V00 |  |  | CRS Status: | C3
Item | Comments (NISOC/PEDCO) |  | Email/letter No. | Comment Date | Clarification (By EPC Contractor) |  |  | Client Conclusion
1 | موازنه جزء آب حول contactor برقرار نمی باشد. |  | PEDCO COMMENTS ON BK-HD-PEDCO-SVTR-MF-0004 | 2024-03-16
2 | دمای فرض شده 58درجه سانتیگراد برای fuel gas مصرفی واحد در summer case صحیح نمی باشد. |  | PEDCO COMMENTS ON BK-HD-PEDCO-SVTR-MF-0004 | 2024-03-16
3 | make-up برای گلایکول مصرفی در نظر گرفته نشده است. |  | PEDCO COMMENTS ON BK-HD-PEDCO-SVTR-MF-0004 | 2024-03-16
4 | دمای دو جریان خروجی شماره 6 و 12 به سمت flare بیشتر از ماکزیمم دمای عملیاتی شبکه flare می باشد. |  | PEDCO COMMENTS ON BK-HD-PEDCO-SVTR-MF-0004 | 2024-03-16
5 | حداقل اطلاعات تجهیزات در قسمت Description بر اساس IPS-E-PR- 170 ارائه شود. |  | PEDCO COMMENTS ON BK-HD-PEDCO-SVTR-MF-0004 | 2024-03-16
Legend | Comment Sheet Status: (By Client) C1: Reviewed with no comment (No Response required) C2: Reviewed with minor comment ( work may proceed and comments to be addressed and incorpated prior to issue) C3: Reviewed with major comment (Revise and resubmit. Work may not be proceeded until the document is returned with code C1 &C2) C4: Rejected ( Deviated from the project requirement. Resubmit for Review) C5: Issued for information (No Response required)
Signature | CLIENT (NISOC/PEDCO) |  |  |  |  | EPC Contractor
| Commented By: M.Esfandani P.bavarsad | Signature | H.Naserizadeh |  |  | Clarified By: | Signature
| Date: 16/03/2024 |  |  |  |  | Date: