## Cover
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0004 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR TEMPERATURE GAUGE نگهداشت و افزایش تولید میدان نفتی بینک
V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
|  |  |  | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0004 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 |  | X | [7 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-TG-2110
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2110 |  |  |  |  | 1
| 2 | Service | [5 empty] | DEHYDRATED GAS TO E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  |  | Piping Class |  |  | GAS-111-0002-FN05-6"-PT |  |  |  |  | FN05
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | GAS |  |  | Vapor
| 6 | Operating Pressure: |  |  |  |  | Unit | 53.1 | [5 empty] | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/59 | [5 empty] | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 66.21 | [5 empty] | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/95 | [5 empty] | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~100 Deg C
| 14 | Instrument Range | [5 empty] | 0~100 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS (NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1 1/2 " |  | 600# |  |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 250mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Length and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2111
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2111 |  |  |  | 1
| 2 | Service | [5 empty] | DEHYDRATED GAS FROM E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class | Piping Class |  |  | GAS-111-01791-FN05-6"-PT |  |  |  | FN05
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | GAS |  |  | Vapor
| 6 | Operating Pressure: |  |  |  |  | Unit | 53.1/53.1 (summer/winter) |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/59 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 65.95/66.87 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/95 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~100 Deg C
| 14 | Instrument Range | [5 empty] | 0~100 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1 1/2 " |  | 600# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 250mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2112
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2112 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-100A/B TO E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class | Piping Class |  |  | TEG-111-0003-FN04-1"-HI (INSTALL ON 90° ELBOW) |  |  |  |  | FN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  |  |  |  | Unit | 55.1/55.1 (summer/winter) |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/62 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 120.45/124.6 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 120.45/124.6 (summer/winter) |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~250 Deg C
| 14 | Instrument Range | [5 empty] | 0~250 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1/2" |  | 600# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2113
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2113 |  |  |  | 1
| 2 | Service | [5 empty] | FROM E-100 TO GLYCOL V-120
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 2/7
| 4 | Line No. / Equipment No. |  | Piping Class | Piping Class |  |  | TEG-111-0007-AN07-1"-HI (INSTALL ON 90° ELBOW) |  |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  |  |  |  | Unit | 4.5/4.5 (summer/winter) |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/8.5 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 73.63/74.53 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/100 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~160 Deg C
| 14 | Instrument Range | [5 empty] | 0~160 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1" |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2114
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2114 |  |  |  | 1
| 2 | Service | [5 empty] | R-100
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class | Piping Class |  |  | R-100 |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  |  |  |  | Unit | 0.3/0.6 (summer/winter) |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/4.1 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 140/204 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/234 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~400 Deg C
| 14 | Instrument Range | [5 empty] | 0~400 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 2" |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 500mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2115
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2115 |  |  |  | 1
| 2 | Service | [5 empty] | FROM C-100 TO E-100
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0007-AN07-1"-HI (INSTALL ON 90° ELBOW) |  |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  |  |  |  | Unit | 4.5/4.5 (summer/winter) |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/8.5 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 62.35 / 62.96 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/100 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~100 Deg C
| 14 | Instrument Range | [5 empty] | 0~100 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1/2" |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2116
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2116 |  |  |  | 1
| 2 | Service | [5 empty] | FROM V-120 TO E-200
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0004-AN04-2"-PT (INSTALL ON 90° ELBOW) |  |  |  |  | AN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  |  |  |  | Unit | 0.3/0.6 |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/5.8 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 191.5/192.7 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/220 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | NO |  |  | NO
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~400 Deg C
| 14 | Instrument Range | [5 empty] | 0~400 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1/2" |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2117
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2117 |  |  |  | 1
| 2 | Service | [5 empty] | TEG FROM E-200 TO C-200
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0027-AN07-1"-HI (INSTALL ON 2" 90° ELBOW) |  |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  |  |  |  | Unit | 3.1 |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/7.5 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 140 |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/165 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~250 Deg C
| 14 | Instrument Range | [5 empty] | 0~250 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1/2" |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2118
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2118 |  |  |  | 1
| 2 | Service | [5 empty] | FROM F-200 TO E-200
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0021-AN07-1"-HI (INSTALL ON 2" 90° ELBOW) |  |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  |  |  |  | Unit | 3.3 |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/7.5 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 73.6/74.52 (Summer/Winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/165 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~160 Deg C
| 14 | Instrument Range | [5 empty] | 0~160 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1" |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm

## D-TG-2119
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE GAUGE
|  | پروژه | بسته کاری |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 12
شماره پیمان:
9184 – 073 - 053 |  | BK | GCS |  | MF |  |  | 120 | IN | DS | 0004 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-TG-2119 |  |  |  | 1
| 2 | Service | [5 empty] | FROM E-200 TO P-100B
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0006-AN04-2"-HI (INSTALL ON 2" 90° ELBOW) |  |  |  |  | AN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  |  |  |  | Unit | 0.2 |  |  |  |  | barg
| 7 | Design Pressure(MIN/MAX) |  |  |  |  | Unit | Full Vacuum/5.8 |  |  |  |  | barg
| 8 | Operating Temperature(MIN/MAX) |  |  |  |  | Unit | 119.43/123.6 (summer/winter) |  |  |  |  | °C
| 9 | Design Temperature(MIN/MAX) |  |  |  |  | Unit | 5/220 |  |  |  |  | °C
| 10 | Corrosive Service |  | NACE Requirement |  |  |  | NO |  |  | NO
| 11 | Toxic Service |  | Solid Particle
THERMOMETER | 12 | Type | [5 empty] | Bi-metallic
| 13 | Calibration Range (Began/End) | [5 empty] | 0~250 Deg C
| 14 | Instrument Range | [5 empty] | 0~250 Deg C
| 15 | Dial Size |  | Dial Color |  |  |  | 150 mm |  |  | Black Letter on White Alu. Plate
| 16 | Case Material | [5 empty] | Aluminium
| 17 | Element Type |  | Element Material |  |  |  | Bi-metallic |  |  | VTA
| 18 | Connection Type |  | Connection Size |  |  |  | Threaded |  |  | 1/2" NPT(M)
| 19 | Pointer Color |  | Pointer Material |  |  |  | Black |  |  | Aluminium
| 20 | Stem Type |  | Stem Material |  |  |  | Union connection |  |  | 316 SS(NACE)
| 21 | Stem Position | [5 empty] | Bottom
| 22 | Stem Length |  | Stem Diameter |  |  |  | VTA |  |  | 6mm
| 23 | Accuracy |  | Ingress Protection |  |  |  | 1% of full scale |  |  | IP65
| 24 | Window Material | [5 empty] | Laminated Safety Glass
| 25 | Over range Protection | [5 empty] | 1.5 times the maximum scale
| 26 | External Calibration Adjustment | [5 empty] | YES (VTC)
| 27 | Adjustable Compression Fitting | [5 empty] | YES (VTC)
| 28 | Form | [5 empty] | Every angle
| 29 | Filled System |  | Type |  |  |  | NA
| 30 |  |  | Compensation |  |  |  | NA
| 31 |  |  | Capillary Length |  |  |  | NA
| 32 |  |  | Capillary Material |  |  |  | NA
| 33 |  |  | Armour Material |  |  |  | NA
| 34 |  |  | Bulb Material |  |  |  | NA
| 35 |  |  | Bulb Length |  |  |  | NA
| 36 |  |  | Bulb Type |  |  |  | NA
| 37 |  |  | Bulb Connection |  |  |  | NA
| 38 |  |  | Bulb SAMA Class |  |  |  | NA
THERMOWELL | 39 | Process Connection |  | Size | Rating | Facing |  | 1/2 " |  | 300# |  | RF (125-250 AARH)
| 40 | Connection Type | [5 empty] | Solid Drilled Bar Stoke Tapered Flange
| 41 | Well & Flange Material | [5 empty] | SS316L(NACE)
| 42 | Instrument Connection | [5 empty] | 1/2" NPT(F)
| 43 | Insertion Length (U) | [5 empty] | 200mm
| 44 | Lagging Extension (T) | [5 empty] | 75 mm
| 45 | Bore Diameter | [5 empty] | 7 mm
| 46 | Tip Thickness | [5 empty] | 5 mm
| 47 | Treatment |  | Coating |  |  |  | VTA |  |  | VTA
| 48 | Finish | [5 empty] | U-length polished to 0.25µm(VTC)
| 49 | Stamping | [5 empty] | On flange (NOTE 2)
| 50 | Standard Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 51 | Anti Abrasion Material |  | Anti Abrasion Thickness (mm) |  |  |  | NA |  |  | NA
| 52 | Screwed Plug and Chain | [5 empty] | NA
| 53 | Outside Diameter@Tip / Outside Diameter@Shank | [5 empty] | VTA
PURCHASE | 54 | Manufacturer | [5 empty] | Will be Selected Later
| 55 | Model | [5 empty] | Will be Selected Later
| 56 | Requisition Number | [5 empty] | Will be Selected Later
Note: 1- Stress Calculation, Wake Frequency Calculation, for Thermowell shall be done. 2- Thermowell material, length, pressure rating and tag number shall be stamped on flange. 3- Engraved stainless steel corrosion resistant tag nameplate is required for thermometer. 4-Vendor shall fully supply & assemble thermowell with temp. indicator 5-VTA: Vendor to advice. VTC: Vendor to confirm N/A:Not Applicable N/R: Not Required 6-Leangth and Thickness of thermowell shall be confirmed by vendor according to stress calculation results. 7-Lines to be swaged to 4" minimum, thermowell length 200 mm 8-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard as per Specification For Piping Material (PMS) 9-Due to fluid service vendor to provide higher grade or proper material for thermowell if reqired,defined material is minimum requirement. 10-Projection of thermowell flange is 150mm from face of pipe flange to surface of pipe or header
T
U
150mm