## Cover
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 11
9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0005 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
|  |  |  | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 11
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0005 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-TIT-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 3 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2101
General | 1 | Service | [5 empty] | WET GAS TO C100
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page1/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 1 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | GAS-111-0001-FN05-6"-PT
Process Conditions | 6 | Fluid | [5 empty] | GAS
| 7 | Phase | [5 empty] | Vapor
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 148 °C
| 10 | Max Temperature | [5 empty] | 60 °C
| 11 | Design Pressure | [5 empty] | F.V. / 62 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 53.9 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 1 1/2", #300 RF(1/2NPT to 1 1/2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 100 ºC |  |  | 0 - 120 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2101
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 600#
| 49 | Process Connection | [5 empty] | 1 1/2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 250mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 4 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2102
General | 1 | Service | [5 empty] | FROM E300 TO C100
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page1/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 2 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | TEG-111-0001-FN04-1"-HI (INSTALL ON 2" 90° ELBOW)
Process Conditions | 6 | Fluid | [5 empty] | TEG
| 7 | Phase | [5 empty] | Liquid
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 145 °C
| 10 | Max Temperature | [5 empty] | 68 °C
| 11 | Design Pressure | [5 empty] | F.V. / 62 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 54.9 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 1", #300 RF(1/2NPT to 1" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 100 ºc |  |  | 0 - 120 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2102
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 600#
| 49 | Process Connection | [5 empty] | 1/2" NPT
| 50 | Flange Facing / Finish | [5 empty] | NA
| 51 | Insertion Length |  |  |  | Lag Extension |  | 200mm(VTA) |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | Yes
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 5 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2103
General | 1 | Service | [5 empty] | DEHYDRATED GAS FROM E300
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page1/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 3 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | GAS-111-01791-FN05-6"-PT
Process Conditions | 6 | Fluid | [5 empty] | GAS
| 7 | Phase | [5 empty] | Vapor
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 95 °C
| 10 | Max Temperature | [5 empty] | 66.87 °C
| 11 | Design Pressure | [5 empty] | F.V. / 59 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 53.1 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 1 1/2", #300 RF(1/2NPT to 1 1/2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 100 ºC |  |  | 0 - 120 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2103
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 600#
| 49 | Process Connection | [5 empty] | 1 1/2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 250mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2104
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 6 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2104
General | 1 | Service | [5 empty] | C100
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page1/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 4 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | NA
Process Conditions | 6 | Fluid | [5 empty] | GAS and TEG
| 7 | Phase | [5 empty] | Vapor / Liquid
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 5 / 148 °C
| 10 | Max Temperature | [5 empty] | 63.6 °C
| 11 | Design Pressure | [5 empty] | F.V. / 62 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 53.8 / 54.9 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 2", #300 RF(1/2NPT to 2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 100 ºC |  |  | 0 - 120 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2104
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 600#
| 49 | Process Connection | [5 empty] | 2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 500mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2105
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 7 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2105
General | 1 | Service | [5 empty] | V120
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page2/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 5 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | NA
Process Conditions | 6 | Fluid | [5 empty] | TEG
| 7 | Phase | [5 empty] | V / L
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 5 / 120 °C
| 10 | Max Temperature | [5 empty] | 74.53 °C
| 11 | Design Pressure | [5 empty] | F.V. / 8 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 4.5 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 2", #300 RF(1/2NPT to 2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 100 ºC |  |  | 0 - 120 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2105
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 300#
| 49 | Process Connection | [5 empty] | 2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 500mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2106
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 8 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2106
General | 1 | Service | [5 empty] | R100
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page4/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 6 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | NA
Process Conditions | 6 | Fluid | [5 empty] | TEG
| 7 | Phase | [5 empty] | V / L
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 5 / 234 °C
| 10 | Max Temperature | [5 empty] | 204 °C
| 11 | Design Pressure | [5 empty] | F.V. / 4.1 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 0.3 / 0.6 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 2", #300 RF(1/2NPT to 2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 -300 ºC |  |  | 0 - 350 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2106
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 300#
| 49 | Process Connection | [5 empty] | 2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 500mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2107
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 9 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2107
General | 1 | Service | [5 empty] | FROM E100 TO LP FLARE
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page4/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX ia IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 7 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | GAS-111-0001-AS00-2"-HI (INSTALL ON 2" 90° ELBOW)
Process Conditions | 6 | Fluid | [5 empty] | TEG
| 7 | Phase | [5 empty] | V / L
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 5 / 234 °C
| 10 | Max Temperature | [5 empty] | 86.85 °C
| 11 | Design Pressure | [5 empty] | F.V. / 4.1 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 0.2/0.6 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 1", #300 RF(1/2NPT to 1" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 120 ºC |  |  | 0 - 150 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2107
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 300#
| 49 | Process Connection | [5 empty] | 1/2" NPT
| 50 | Flange Facing / Finish | [5 empty] | NA
| 51 | Insertion Length |  |  |  | Lag Extension |  | 200mm (VTA) |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2108
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 10 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2108
General | 1 | Service | [5 empty] | R100
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page4/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX i IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 8 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | NA
Process Conditions | 6 | Fluid | [5 empty] | TEG
| 7 | Phase | [5 empty] | V / L
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 535 °C
| 10 | Max Temperature | [5 empty] | 510 °C
| 11 | Design Pressure | [5 empty] | F.V. / 3.5 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 1 bara
Element | 13 | Type | [5 empty] | Thermocouple
| 14 | T/C |  | Element Type |  |  |  | K TYPE
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | YES
| 17 |  |  | Wire Size |  |  |  | 0,70 According to IEC 61515
| 18 | RTD |  | Material |  |  |  | N/A
| 19 |  |  | Resistance |  |  |  | N/A
| 20 |  |  | Wire Size |  |  |  | N/A
| 21 | Accuracy | [5 empty] | IEC 60584-2 class 1
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | INCONEL600
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 2", #300 RF(1/2NPT to 2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 800 ºC |  |  | 0 - 1200 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2108
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 300#
| 49 | Process Connection | [5 empty] | 2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 500mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS

## D-TIT-2109
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR TEMPERATURE TRANSMITTER
شماره پیمان: | پروژه |  | بسته کاری |  |  |  | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه | شماره صفحه: 11 از 11
9184 – 073 - 053 | BK |  | GCS |  |  |  | MF |  | 120 | IN | DS | 0005 |  | V00
Tag No: | [7 empty] | D-TIT-2109
General | 1 | Service | [5 empty] | R100
| 2 | P&ID No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 (Page4/7)
| 3 | Area Classification | [5 empty] | ZONE 2 EX i IIB T4
| 4 | Equipment No. |  |  |  | Quantity |  | 9 |  |  |  |  | 1
| 5 | Line No. | [5 empty] | NA
Process Conditions | 6 | Fluid | [5 empty] | TEG
| 7 | Phase | [5 empty] | V / L
| 8 | Ambient Temperature | [5 empty] | 5 / 50 °C (min/max)
| 9 | Design Temperature | [5 empty] | 5 / 234 °C
| 10 | Max Temperature | [5 empty] | 204 °C
| 11 | Design Pressure | [5 empty] | F.V. / 4.1 barg
| 12 | Min/Nor/Max Pressure | [5 empty] | 0.3 / 0.6 barg
Element | 13 | Type | [5 empty] | RTD-Pt100 (3 wire)
| 14 | T/C |  | Element Type |  |  |  | N/A
| 15 |  |  | Grounded |  |  |  | N/A
| 16 |  |  | Ungrounded |  |  |  | N/A
| 17 |  |  | Wire Size |  |  |  | N/A
| 18 | RTD |  | Material |  |  |  | RTD(platinum resistance temperature detector)
| 19 |  |  | Resistance |  |  |  | VTA
| 20 |  |  | Wire Size |  |  |  | VTA
| 21 | Accuracy | [5 empty] | IEC-60751
| 22 | Single / Double or Other | [5 empty] | DOUBLE
| 23 | Sheath Material | [5 empty] | Platinum
| 24 | Sheath OD | [5 empty] | Φ6
| 25 | Stem Length | [5 empty] | VTA
| 26 | Insulating Material | [5 empty] | Magnesium Oxide
| 27 | Reference Standard | [5 empty] | IEC 60584
| 28 | Connection | [5 empty] | FLG, 2", #300 RF(1/2NPT to 2" FLG)
29
Transmitter | 30 | Transmitter type | [5 empty] | 2 wire(VTC)
| 31 | Calibration Range |  |  |  | Instrument Range |  | 0 - 300 ºC |  |  | 0 - 350 ºC
| 32 | Integral Indicator | [5 empty] | Yes
| 33 | Failure / Diagnostic Alarm | [5 empty] | Self Diagnostic (VTC)
| 34 | Output Signal |  |  |  | Linearization |  | 4-20mA Hart |  |  | Yes (VTA)
| 35 | Accuracy | [5 empty] | ±0.1 % FS
| 36 | Power Supply |  |  |  | Power Consumption |  | Loop Powered 24VDC |  |  | 1W(VTA)
| 37 | Housing Material |  |  |  | Mounting Type |  | Painted Die Cast Aluminum |  |  | Head Mounted
| 38 | Electrical Connection |  |  |  | RFI Protection |  | M20 x 1.5 |  |  | Yes (VTA)
| 39 | Write Protection | [5 empty] | YES
| 40 | Ex Certificate |  |  |  | SIL |  | ZONE 2 EX ia IIB T4 |  |  | NA
| 41 | Ingress Protection | [5 empty] | IP65
42
Well | 43 | Tag | [5 empty] | D-TW-2109
| 44 | Reference Standard | [5 empty] | ASME PTC 19.3
| 45 | Construction Type | [5 empty] | Solid Drilled Bar Stoke Tapered
| 46 | Element Connection | [5 empty] | NPT
| 47 | Size | [5 empty] | 1/2”
| 48 | Rating | [5 empty] | 300#
| 49 | Process Connection | [5 empty] | 2" FLG
| 50 | Flange Facing / Finish | [5 empty] | RF
| 51 | Insertion Length |  |  |  | Lag Extension |  | 500mm |  |  | 75mm
| 52 | Flange Material | [5 empty] | SS316L
| 53 | Well Material | [5 empty] | SS316L
| 54 | Mounting Sketch | [5 empty] | Vertical
| 55 | NACE Requirements | [5 empty] | YES
Management Data | 56 | Model |  |  | Manufacturer |  |  | Will be finalized later |  |  |  | Will be finalized later
| 57 | Drawing Number | [5 empty] | BK-GCS-MF-120-IN-DW-0005
| 58 | Bracket/Material | [5 empty] | 2" Pipe mounted Bracket / 316 SS