## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 26
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0006 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 26
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0006 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 |  | X | [7 empty] | 72
13 |  | X | [7 empty] | 73
14 |  | X | [7 empty] | 74
15 |  | X | [7 empty] | 75
16 |  | X | [7 empty] | 76
17 |  | X | [7 empty] | 77
18 |  | X | [7 empty] | 78
19 |  | X | [7 empty] | 79
20 |  | X | [7 empty] | 80
21 |  | X | [7 empty] | 81
22 |  | X | [7 empty] | 82
23 |  | X | [7 empty] | 83
24 |  | X | [7 empty] | 84
25 |  | X | [7 empty] | 85
26 |  | X | [7 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-PG-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 26
053-073-9184 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-PG-2101 |  |  |  | 1
| 2 | Service | [5 empty] | FROM C-100 TO E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | GAS-111-0002-FN05-6"-PT |  |  |  | FN05
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | GAS |  |  | Vapor
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 53.8 |  |  | 54.9 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 63.62 |  |  | 63.89 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 59 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 95 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01418 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 100 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 2 | D-PG-2102 |  |  |  | 1
| 2 | Service | [5 empty] | DEHYDRATED GAS FROM E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | GAS-111-01791-FN05-6"-PT |  |  |  | FN05
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | GAS |  |  | Vapor
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 53.1 |  |  | 53.1 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 65.95 |  |  | 66.87 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 59 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 95 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.0142 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 100 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 3 | D-PG-2103 |  |  |  | 1
| 2 | Service | [5 empty] | DEHYDRATED GAS FROM E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | C100 |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | GAS |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 53.8 |  |  | 54.9 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 63.62 |  |  | 63.89 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 62 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 148 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01418 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 100 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2105
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 4 | D-PG-2105 |  |  |  | 1
| 2 | Service | [5 empty] | LEAN GLYCOL FROM E-300 TO C-100
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0001-FN04-1"-HI |  |  |  | FN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 54.9 |  |  | 65.9 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 68 |  |  | 82 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 62 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 145 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 7.924 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | YES
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 100 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2106
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 5 | D-PG-2106 |  |  |  | 1
| 2 | Service | [5 empty] | FROM E-100 TO V-120
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 2/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0007-AN07-1"-HI |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.5 |  |  | 4.5 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 68 |  |  | 68 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 8.5 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 100 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01269 (vapor) and 5.331 (Liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2107
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 6 | D-PG-2107 |  |  |  | 1
| 2 | Service | [5 empty] | FROM C-100 TO E-100
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0001-AN07-1"-HI |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.5 |  |  | 4.5 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 62.35 |  |  | 62.96 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 8.5 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 100 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01269 (vapor) and 5.331 (Liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2108
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 7 | D-PG-2108 |  |  |  | 1
| 2 | Service | [5 empty] | R-100
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | R100 |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 0.3 |  |  | 0.6 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 140 |  |  | 204 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 4.1 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 234 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01092 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Diaphragm
| 17 | Range |  |  |  |  | Unit | 0 ~ 1 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | YES (coiled type)
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2109
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 8 | D-PG-2109 |  |  |  | 1
| 2 | Service | [5 empty] | FROM FUEL GAS HEADER TO BURNER
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | FLG-111-0024-AN07-1"-PT |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | FUEL GAS |  |  | V
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.9 |  |  | 4.9 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 48 |  |  | 48 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | 9 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 85 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01147 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | -
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2110
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 9 | D-PG-2110 |  |  |  | 1
| 2 | Service | [5 empty] | FROM FUEL GAS HEADER TO REBOILER
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | FLG-111-0024-AN07-1"-PT |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | FUEL GAS |  |  | V
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.9 |  |  | 4.9 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 48 |  |  | 48 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | 9 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 85 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01147 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | -
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Manufacturer/Model | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2111
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 10 | D-PG-2111 |  |  |  | 1
| 2 | Service | [5 empty] | FROM V-130 TO E-200
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0004-AN04-2"-PT |  |  |  | AN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 0.3 |  |  | 0.6 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 191.5 |  |  | 192.7 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 5.8 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 220 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.67 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | NO
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | NO
GAUGE | 16 | Pressure Element Type | [5 empty] | Diaphragm
| 17 | Range |  |  |  |  | Unit | 0 ~ 1 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | YES (coiled type)
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | NA
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2112
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 13 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 11 | D-PG-2112 |  |  |  | 1
| 2 | Service | [5 empty] | FROM E-200 TO C-200
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0027-AN07-1"-HI |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 3.1 |  |  | 3.1 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 140 |  |  | 140 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 7.5 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 165 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 1.3908 (liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 6 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | YES (coiled type)
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2113
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 14 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 12 | D-PG-2113 |  |  |  | 1
| 2 | Service | [5 empty] | FROM F-200 TO E-200
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0021-AN07-1"-HI |  |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 3.3 |  |  | 3.3 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 73.6 |  |  | 74.52 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 7.5 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 165 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 5.36 (liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 6 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2114
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 15 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 13 | D-PG-2114 |  |  |  | 1
| 2 | Service | [5 empty] | FROM E-200 TO P-100-B
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0006-AN04-2"-HI |  |  |  | AN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 0.2 |  |  | 0.2 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 119.43 |  |  | 123.6 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 5.8 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 220 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 2.15 / 2.36 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | NO
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | NO
GAUGE | 16 | Pressure Element Type | [5 empty] | Diaphragm
| 17 | Range |  |  |  |  | Unit | 0 ~ 0.6 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | YES (coiled type)
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2115
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 16 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 14 | D-PG-2115 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-100-A TO E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0004-FN04-1"-HI |  |  |  | FN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 55.1 |  |  | 55.1 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 120.45 |  |  | 124.6 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 62 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 145 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 2.11 / 2.31 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | -
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | -
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 100 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | YES (coiled type)
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2116
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 17 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 15 | D-PG-2116 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-100-B TO E-300
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0006-AN04-2"-HI |  |  |  | AN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | Liquid
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 55.1 |  |  | 55.1 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 120.45 |  |  | 124.6 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 62 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 145 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 2.11 / 2.31 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | -
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | -
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 100 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | YES (coiled type)
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2117
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 18 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 16 | D-PG-2117 |  |  |  | 1
| 2 | Service | [5 empty] | FUEL GAS TO REBOILER
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 5/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0005-FN04-1"-HI |  |  |  | FN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | FUEL GAS |  |  | V
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.9 |  |  | 4.9 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 48 |  |  | 48 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | 9 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 85 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01147 |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | -
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | -
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2118
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 19 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 17 | D-PG-2118 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-200-A TO TO LEAN GLYCOL PUMP'S SUCTION LINE
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 6/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | CHM-111-0005-AS00-1"-HI |  |  |  | AS00
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | Will be finalized later |  |  | Will be finalized later
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 9 | Design Pressure |  |  |  |  | Unit | Will be finalized later
| 10 | Design Temperature |  |  |  |  | Unit | Will be finalized later
| 11 | Operating Viscosity |  |  |  |  | Unit | Will be finalized later
| 12 | Pulsation | [5 empty] | Will be finalized later
| 13 | Corrosive Service | [5 empty] | Will be finalized later
| 14 | Toxic Service | [5 empty] | Will be finalized later
| 15 | NACE Requirement | [5 empty] | Will be finalized later
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | Will be finalized later |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | Cast Aluminum |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 1% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2119
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 20 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 18 | D-PG-2119 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-200-B TO TO LEAN GLYCOL PUMP'S SUCTION LINE
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 6/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | CHM-111-0005-AS00-1"-HI |  |  |  | AS00
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | Will be finalized later |  |  | Will be finalized later
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 9 | Design Pressure |  |  |  |  | Unit | Will be finalized later
| 10 | Design Temperature |  |  |  |  | Unit | Will be finalized later
| 11 | Operating Viscosity |  |  |  |  | Unit | Will be finalized later
| 12 | Pulsation | [5 empty] | Will be finalized later
| 13 | Corrosive Service | [5 empty] | Will be finalized later
| 14 | Toxic Service | [5 empty] | Will be finalized later
| 15 | NACE Requirement | [5 empty] | Will be finalized later
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | Will be finalized later |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | Cast Aluminum |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 1% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2120
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 21 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 19 | D-PG-2120 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-300-A TO TO LEAN GLYCOL PUMP'S SUCTION LINE
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 7/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | CHM-111-0006-AS00-1"-HI |  |  |  | AS00
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | Will be finalized later |  |  | Will be finalized later
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 9 | Design Pressure |  |  |  |  | Unit | Will be finalized later
| 10 | Design Temperature |  |  |  |  | Unit | Will be finalized later
| 11 | Operating Viscosity |  |  |  |  | Unit | Will be finalized later
| 12 | Pulsation | [5 empty] | Will be finalized later
| 13 | Corrosive Service | [5 empty] | Will be finalized later
| 14 | Toxic Service | [5 empty] | Will be finalized later
| 15 | NACE Requirement | [5 empty] | Will be finalized later
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | Will be finalized later |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | Cast Aluminum |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 1% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PG-2121
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 22 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 20 | D-PG-2121 |  |  |  | 1
| 2 | Service | [5 empty] | FROM P-300-B TO TO LEAN GLYCOL PUMP'S SUCTION LINE
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 7/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | CHM-111-0006-AS00-1"-HI |  |  |  | AS00
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | Will be finalized later |  |  | Will be finalized later
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | Will be finalized later |  |  | Will be finalized later
| 9 | Design Pressure |  |  |  |  | Unit | Will be finalized later
| 10 | Design Temperature |  |  |  |  | Unit | Will be finalized later
| 11 | Operating Viscosity |  |  |  |  | Unit | Will be finalized later
| 12 | Pulsation | [5 empty] | Will be finalized later
| 13 | Corrosive Service | [5 empty] | Will be finalized later
| 14 | Toxic Service | [5 empty] | Will be finalized later
| 15 | NACE Requirement | [5 empty] | Will be finalized later
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | Will be finalized later |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | Cast Aluminum |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS
| 24 | Socket Material | [5 empty] | 316 SS
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 1% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Process Connection | [5 empty] | NA
| 34 | Connection Material |  | Connection Rating |  |  |  | NA |  |  | NA
| 35 | Extended Length | [5 empty] | NA
| 36 | Diaphragm Material | [5 empty] | NA
| 37 | Bottom Housing Material | [5 empty] | NA
| 38 | Fill Fluid | [5 empty] | NA
| 39 | Capillary Length | [5 empty] | NA
| 40 | Capillary Bleeder | [5 empty] | NA
| 41 | Capillary Material | [5 empty] | NA
| 42 | Flushing Connection | [5 empty] | NA
| 43 | Top Housing Material | [5 empty] | NA
| 44 | Instrument Connection | [5 empty] | NA
| 45 | Fill Connection | [5 empty] | NA
| 46 | Model Number | [5 empty] | NA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | NA
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | 2-Way Valve Manifold |  |  | Will be finalized later
| 54 | Body Material |  | Trim Material |  |  |  | 316 SS |  |  | 316 SS
| 55 | Process Connection |  | Instrument Connection |  |  |  | 1/2" NPT(F) |  |  | 1/2" NPT(F)
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | 1/4" NPT(F) |  |  | 3000#
| 57 | Packing Material | [5 empty] | PTFE (VTC)
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PDG-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 23 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 21 | D-PDG-2101 |  |  |  | 1
| 2 | Service | [5 empty] | F-100-A
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 3/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | F-100-A |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.5 |  |  | 4.5 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 73.63 |  |  | 74.53 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 8 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 100 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 5.369 (liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | VTA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PDG-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 24 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 22 | D-PDG-2102 |  |  |  | 1
| 2 | Service | [5 empty] | F-100-B
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 3/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | F-100-B |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 4.5 |  |  | 4.5 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 73.63 |  |  | 74.53 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 8 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 100 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 5.369 (liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 10 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | VTA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PDG-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 25 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 23 | D-PDG-2103 |  |  |  | 1
| 2 | Service | [5 empty] | F-200-A
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 3/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | F-200-A |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 3.8 |  |  | 3.8 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 73.63 |  |  | 74.53 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 7.5 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 100 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 5.369 (liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 6 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.

## D-PDG-2104
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR PRESSURE GAUGES AND DIFF. PRESSURE GAUGES
شماره پیمان: | پروژه | بسته کاری | صادرکننده |  | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 26 از 26
9184 – 073 - 053 | BK | GCS | MF |  | 120 |  | IN | DS | 0006 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 24 | D-PDG-2104 |  |  |  | 1
| 2 | Service | [5 empty] | F-200-B
| 3 | P & ID No. |  | Page |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 3/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | F-200-B |  |  |  | NA
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  | V / L
| 6 | Operating Pressure: |  | Normal | Maximum |  | Unit | 3.8 |  |  | 3.8 |  | barg
| 7 | Operating Diff. Pressure: |  | Normal | Maximum |  | Unit | - |  |  | - |  | barg
| 8 | Operating Temperature: |  | Normal | Maximum |  | Unit | 73.63 |  |  | 74.53 |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 7.5 |  |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit | 5 / 100 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 5.369 (liquid) |  |  |  |  | cp
| 12 | Pulsation | [5 empty] | -
| 13 | Corrosive Service | [5 empty] | YES
| 14 | Toxic Service | [5 empty] | -
| 15 | NACE Requirement | [5 empty] | YES
GAUGE | 16 | Pressure Element Type | [5 empty] | Bourdon Tube
| 17 | Range |  |  |  |  | Unit | 0 ~ 6 |  |  |  |  | Barg
| 18 | Zero Adjustment | [5 empty] | Yes
| 19 | Mounting | [5 empty] | Local
| 20 | Dial Size |  | Dial Color |  |  |  | 150 |  |  | White laminated with black numerals and markings
| 21 | Case Material |  | Window Material (Lens) |  |  |  | 316 SS |  |  | Shatterproof
| 22 | Ring Construction |  | Ring Material |  |  |  | Screwed Ring |  |  | 316 SS
| 23 | Pressure Element Material | [5 empty] | 316 SS (NACE)
| 24 | Socket Material | [5 empty] | 316 SS (NACE)
| 25 | Connection Size |  | Connection Location |  |  |  | 1/2" NPT(M) |  |  | Bottom
| 26 | Movement Material | [5 empty] | 316 SS (NACE)
| 27 | Nominal Accuracy | [5 empty] | +/- 0.5% of F.S
| 28 | Micrometer Pointer | [5 empty] | Aluminium , Black
| 29 | Blow-Out Protection | [5 empty] | Rubber Blow-out Protection on the Back
| 30 | Over range Protection | [5 empty] | 1.3 Full-Scale
| 31 | Ingress Protection | [5 empty] | IP 65
| 32 | Manufacturer/Model | [5 empty] | Will be finalized later
DIAPHRAGM SEAL | 33 | Type |  | Process Connection |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | 2" Flanged type
| 34 | Connection Material |  | Connection Rating |  |  |  | 316 SS (NACE) |  |  | 600#
| 35 | Extended Length | [5 empty] | VTA
| 36 | Diaphragm Material | [5 empty] | 316 SS (NACE)
| 37 | Bottom Housing Material | [5 empty] | 317 SS (NACE)
| 38 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 39 | Capillary Length | [5 empty] | 3m(VTC)
| 40 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 41 | Capillary Material | [5 empty] | 316 SS (NACE)
| 42 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 43 | Top Housing Material | [5 empty] | 316 SS (NACE)
| 44 | Instrument Connection | [5 empty] | 1/2" NPTF(To Capillary)
| 45 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 46 | Manufacturer/Model | [5 empty] | VTA
OPTIONS | 47 | Siphon | [5 empty] | NA
| 48 | Snubber |  | Material |  |  |  | NA |  |  | NA
| 49 | Over Pressure Protector |  | Material |  | Setting |  | NA | NA |  | NA
| 50 | Oil Filled | [5 empty] | Silicone oil (VTC)
| 51 | Pulsation Dampener | [5 empty] | NA
| 52 | Solid Front | [5 empty] | YES
MANIFOLD | 53 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 54 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 55 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 56 | Vent/Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 57 | Packing Material | [5 empty] | NA
PURCHASE | 58 | Manufacturer | [5 empty] | Will be finalized later
| 59 | Model | [5 empty] | Will be finalized later
60
Note: 1-Engraved stainless steel corrosion resistant tag name plate has to be securely fitted to each instrument,provided with the instrument tag number. 2-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard 3-Pressure gauges shall be able to withstand 1.3 times the maximum process design rating. When this is not possible gauge protection devices may be employed. 4-All the pressure gauges shall be scaled in BARG & PSIG.