## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW ELEMENTS
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0009 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR FLOW ELEMENTS نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW ELEMENTS
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0009 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 | [9 empty] | 66
7 | [9 empty] | 67
8 | [9 empty] | 68
9 | [9 empty] | 69
10 | [9 empty] | 70
11 | [9 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-FE-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW ELEMENTS
شماره پیمان: |  |  | پروژه |  | بسته کاری |  |  |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 3 از 5
9184 – 073 - 053 |  |  | BK |  | GCS |  |  |  | MF |  |  | 120 | IN | DS | 0009 | V00
ORIFICE ASSEMBLY
GENERAL | 1 | Tag Number |  |  |  | Item No. |  |  |  |  | D-FE-2101 |  |  |  |  | 1
| 2 | P & ID No. |  |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  |  | 1/7
| 3 | Service | [8 empty] | FROM E300 TO C100
| 4 | Pipe Size | [8 empty] | 1 "
| 5 | Line No. |  |  |  | Piping Class |  |  | Line Schedule |  | TEG-111-0001-FN04-1"-HI |  |  |  |  | FN04
PROCESS CONDITIONS | 6 | Fluid |  |  |  | Phase |  |  |  |  | TEG |  |  |  |  | Liquid
| 7 | Flow: | [8 empty] | Minimum |  |  | Normal |  |  | Maximum
[10 empty] | Unit | 620 |  |  | 775 |  |  | 930 |  | Kg/h
| 8 | Temperature: |  | Minimum |  | Normal |  | Maximum |  | Unit | 20 |  |  | 68 |  |  | 130 |  | ˚C
| 9 | Pressure: |  | Minimum |  | Normal |  | Maximum |  | Unit | 50 |  |  | 54.9 |  |  | 60 |  | barg
| 10 | Design Temperature | [7 empty] | Unit | 5 / 145 | [7 empty] | ˚C
| 11 | Design Pressure | [7 empty] | Unit | F.V. / 62 | [7 empty] | barg
| 12 | Full Scale Flow | [7 empty] | Unit | 1100
| 13 | Pressure Loss Maximum | [7 empty] | Unit | -
| 14 | Operating Density | [7 empty] | Unit | 1045.15 | [7 empty] | kg/m3
| 15 | Compressibility Factor (Z) | [8 empty] | 0.0221
| 16 | Molecular Weight |  |  |  | Cp / Cv |  |  |  |  | 147.91 |  |  |  |  | 1.045
| 17 | Maximum Velocity | [7 empty] | Unit | 1 | [7 empty] | m/s
| 18 | Quality % or Superheat (YES/NO) |  |  |  | Operating Viscosity |  |  |  | Unit | NO |  |  |  |  | 7.924 |  |  | cp
| 19 | Vaccum Possibility (YES/NO) |  |  |  | Cold Service (YES/NO) |  |  |  |  | - |  |  |  |  | -
| 20 | Comply with NACE MR0175 (YES/NO) | [8 empty] | YES
| 21 | Vapor Pressure | [7 empty] | Unit | 0.1817 | [7 empty] | barg
LINE | 22 | Material | [8 empty] | ASTM A106 GR.B(NACE)
| 23 | Inside Diameter / Outside Diameter | [8 empty] | 20.92 |  |  |  |  | 33.4
| 24 | Piping Line Insulation | [8 empty] | N/A
BASIS | 25 | Type / Pressure Taps | [8 empty] | Flange Tapping |  |  |  |  | 2 TAPS
| 26 | Flow Rate Range | [7 empty] | Unit | 0~1000 | [7 empty] | Kg/hr
| 27 | Differential Pressure @ Full scale | [8 empty] | 0 ~ 250 mbar
28
ORIFICE PLATE | 29 | Size and Flange Rating | [8 empty] | 1" |  |  |  |  | 600#
| 30 | Bore Diameter(d) | [8 empty] | 14.362 mm(VTC)
| 31 | Diameter Ratio(beta=d/D) | [8 empty] | 0.43(VTC)
| 32 | Material | [8 empty] | 316 SS (NACE)
| 33 | Thickness | [8 empty] | 3.2 mm (VTC)
| 34 | Ring Material and Type | [8 empty] | N/A |  |  |  |  | N/A
| 35 | Drain or Vent / Hole Size | [8 empty] | Drain/2mm(VTC)
| 36 | Actual Pressure Loss | [7 empty] | Unit | (VTC) | [7 empty] | mbar
| 37 | Applicable Standard | [8 empty] | ISO-5167/5168
ORIFICE FLANGES | 38 | Type | [8 empty] | Weld neck type
| 39 | Size, Rating and Facing | [8 empty] | 1" |  |  |  |  | 600# RF
| 40 | Flange Face Finish | [8 empty] | 125-250 AARH
| 41 | Flange Material | [8 empty] | ASTM A105
| 42 | Bolts and Nuts Material | [8 empty] | STUD BOLTS TO ASTM A193 GR.B7M,NUTS TO ASTM A194 GR.2HM
| 43 | Gasket Material | [8 empty] | Spiral Wound, 4.45mm,S.S 316 Winding/Graphite Filler,C.S. Outer& S.S 316L Inner Ring , ASME B16.20
| 44 | Jack Screw Material | [8 empty] | YES / ASTM A193-B7M
| 45 | Nipple Type for Press. Tap |  |  |  | Material |  |  |  | Qty. | TBE (L-150mm) /3000# /1/2" NPTM | [5 empty] | ASTM A106 GR.B |  | 2
| 46 | Pressure Taps Size |  |  |  |  | Orientation |  |  |  | 1/2" NPTF |  |  |  |  | 45º (Downward)
47
METER RUN | 48 | Upstream Length |  |  | Downstream Length |  |  |  |  | Unit | 20D(VTA) |  |  |  | 5D(VTA) |  |  |  | mm
| 49 | Material |  |  | End Connection | [5 empty] | 316SS(NACE) |  |  |  |  | 1", 600# RF
| 50 | Straightening Vane | [8 empty] | N/A
PURCHASE | 51 | Manufacturer | [8 empty] | Will be finalized later
| 52 | Model | [8 empty] | Will be finalized later
| 53 | Requisition Number | [8 empty] | -
54
NOTES: 1-Orifice tag number, material, nominal diameter and bore diameter shall be permanently stamped on the orifice plate handle. 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable.

## D-FE-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW ELEMENTS
شماره پیمان: |  |  | پروژه |  | بسته کاری |  |  |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 4 از 5
9184 – 073 - 053 |  |  | BK |  | GCS |  |  |  | MF |  |  | 120 | IN | DS | 0009 | V00
ORIFICE ASSEMBLY
GENERAL | 1 | Tag Number |  |  |  | Item No. |  |  |  |  | D-FE-2102 |  |  |  |  | 1
| 2 | P & ID No. |  |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  |  | 1/7
| 3 | Service | [8 empty] | WET GAS TO C100
| 4 | Pipe Size | [8 empty] | 6 "
| 5 | Line No. |  |  |  | Piping Class |  |  | Line Schedule |  | GAS-111-0001-FN05-6"-PT |  |  |  |  | FN04
PROCESS CONDITIONS | 6 | Fluid |  |  |  | Phase |  |  |  |  | GAS |  |  |  |  | Vapor
| 7 | Flow: | [8 empty] | Minimum |  |  | Normal |  |  | Maximum
[10 empty] | Unit | 12136.72 |  |  | 15170.9 (winter) / 17252.5 (summer) |  |  | 20703 |  | Kg/h
| 8 | Temperature: |  | Minimum |  | Normal |  | Maximum |  | Unit | 59 |  |  | 60 |  |  | 61 |  | ˚C
| 9 | Pressure: |  | Minimum |  | Normal |  | Maximum |  | Unit | 48 |  |  | 53.9 |  |  | 57 |  | barg
| 10 | Design Temperature | [7 empty] | Unit | 148 | [7 empty] | ˚C
| 11 | Design Pressure | [7 empty] | Unit | F.V. / 62 | [7 empty] | barg
| 12 | Full Scale Flow | [7 empty] | Unit | -
| 13 | Pressure Loss Maximum | [7 empty] | Unit | -
| 14 | Operating Density | [7 empty] | Unit | 57.70 | [7 empty] | kg/m3
| 15 | Compressibility Factor (Z) | [8 empty] | 0.9863
| 16 | Molecular Weight |  |  |  | Cp / Cv |  |  |  |  | 24.56 |  |  |  |  | 1.219
| 17 | Maximum Velocity | [7 empty] | Unit | 6 | [7 empty] | m/s
| 18 | Quality % or Superheat (YES/NO) |  |  |  | Operating Viscosity |  |  |  | Unit | NO |  |  |  |  | 0.01275 |  |  | cp
| 19 | Vaccum Possibility (YES/NO) |  |  |  | Cold Service (YES/NO) |  |  |  |  | YES |  |  |  |  | NO
| 20 | Comply with NACE MR0175 (YES/NO) | [8 empty] | YES
| 21 | Vapor Pressure | [7 empty] | Unit | 53.9
LINE | 22 | Material | [8 empty] | ASTM A106 GR.B (NACE)
| 23 | Inside Diameter / Outside Diameter | [8 empty] | 146.329 |  |  |  |  | 168.275
| 24 | Piping Line Insulation | [8 empty] | N/A
BASIS | 25 | Type / Pressure Taps | [8 empty] | Flange Tapping |  |  |  |  | 2 TAPS
| 26 | Flow Rate Range | [7 empty] | Unit | 0 - 22000 | [7 empty] | Kg/hr
| 27 | Differential Pressure @ Full scale | [8 empty] | 0 ~ 250 mbar
28
ORIFICE PLATE | 29 | Size and Flange Rating | [8 empty] | 6" |  |  |  |  | 600#
| 30 | Bore Diameter(d) | [8 empty] | 100.965 mm(VTC)
| 31 | Diameter Ratio(beta=d/D) | [8 empty] | 0.6(VTC)
| 32 | Material | [8 empty] | 316 SS(NACE)
| 33 | Thickness | [8 empty] | 3.2 mm (VTC)
| 34 | Ring Material and Type | [8 empty] | N/A |  |  |  |  | N/A
| 35 | Drain or Vent / Hole Size | [8 empty] | Vent,Drain/2mm(VTC)
| 36 | Actual Pressure Loss | [7 empty] | Unit | (VTC) | [7 empty] | mbar
| 37 | Applicable Standard | [8 empty] | ISO-5167/5168
ORIFICE FLANGES | 38 | Type | [8 empty] | Weld neck type
| 39 | Size, Rating and Facing | [8 empty] | 6" |  |  |  |  | 600# RF
| 40 | Flange Face Finish | [8 empty] | 125-250 AARH
| 41 | Flange Material | [8 empty] | ASTM A105 (NACE)
| 42 | Bolts and Nuts Material | [8 empty] | STUD BOLTS TO ASTM A193 GR.B7M,NUTS TO ASTM A194 GR.2HM
| 43 | Gasket Material | [8 empty] | Spiral Wound, 4.45mm,S.S 316 Winding/Graphite Filler,C.S. Outer& S.S 316L Inner Ring , ASME B16.20
| 44 | Jack Screw Material | [8 empty] | YES / ASTM A193-B7M
| 45 | Nipple Type for Press. Tap |  |  |  | Material |  |  |  | Qty. | TBE (L-150mm) /3000# /1/2" NPTM | [5 empty] | ASTM A106 GR.B |  | 2
| 46 | Pressure Taps Size |  |  |  |  | Orientation |  |  |  | 1/2" NPTF |  |  |  |  | 45º (upward)
47
METER RUN | 48 | Upstream Length / Downstream Length | [7 empty] | Unit | N/A |  |  |  | N/A |  |  |  | mm
| 49 | Material / End Connection | [8 empty] | N/A |  |  |  |  | N/A
| 50 | Straightening Vane | [8 empty] | N/A
PURCHASE | 51 | Manufacturer | [8 empty] | Will be finalized later
| 52 | Model | [8 empty] | Will be finalized later
| 53 | Requisition Number | [8 empty] | -
54
NOTES: 1-Orifice tag number, material, nominal diameter and bore diameter shall be permanently stamped on the orifice plate handle. 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable.

## D-FE-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW ELEMENTS
شماره پیمان: |  |  | پروژه |  | بسته کاری |  |  |  | صادر کننده |  |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 5 از 5
9184 – 073 - 053 |  |  | BK |  | GCS |  |  |  | MF |  |  | 120 | IN | DS | 0009 | V00
ORIFICE ASSEMBLY
GENERAL | 1 | Tag Number |  |  |  | Item No. |  |  |  |  | D-FE-2103 |  |  |  |  | 1
| 2 | P & ID No. |  |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  |  | 4/7
| 3 | Service | [8 empty] | STRIPPING GAS TO R100
| 4 | Pipe Size | [8 empty] | 1 "
| 5 | Line No. |  |  |  | Piping Class |  |  | Line Schedule |  | FLG-111-0028-AN04-1"-PT |  |  |  |  | AN04
PROCESS CONDITIONS | 6 | Fluid |  |  |  | Phase |  |  |  |  | FUEL GAS |  |  |  |  | Vapor
| 7 | Flow: | [8 empty] | Minimum |  |  | Normal |  |  | Maximum
[10 empty] | Unit | 36 |  |  | 45 (winter) / 60 (summer) |  |  | 72 |  | Kg/h
| 8 | Temperature: |  | Minimum |  | Normal |  | Maximum |  | Unit | 15 |  |  | 19/36.78 |  |  | 43.2 |  | ˚C
| 9 | Pressure: |  | Minimum |  | Normal |  | Maximum |  | Unit | 0.5 |  |  | 4.9 |  |  | 5.5 |  | barg
| 10 | Design Temperature | [7 empty] | Unit | 85 | [7 empty] | ˚C
| 11 | Design Pressure | [7 empty] | Unit | 9 | [7 empty] | barg
| 12 | Full Scale Flow | [7 empty] | Unit | -
| 13 | Pressure Loss Maximum | [7 empty] | Unit | -
| 14 | Operating Density | [7 empty] | Unit | 4.015 | [7 empty] | kg/m3
| 15 | Compressibility Factor (Z) | [8 empty] | 0.9863
| 16 | Molecular Weight |  |  |  | Cp / Cv |  |  |  |  | 24.53 |  |  |  |  | 1.219
| 17 | Maximum Velocity | [7 empty] | Unit | 8 | [7 empty] | m/s
| 18 | Quality % or Superheat (YES/NO) |  |  |  | Operating Viscosity |  |  |  | Unit | NO |  |  |  |  | 0.01272
| 19 | Vaccum Possibility (YES/NO) |  |  |  | Cold Service (YES/NO) |  |  |  |  | YES |  |  |  |  | NO
| 20 | Comply with NACE MR0175 (YES/NO) | [8 empty] | YES
| 21 | Vapor Pressure | [7 empty] | Unit | 4.9
LINE | 22 | Material | [8 empty] | ASTM A106 GR.B
| 23 | Inside Diameter / Outside Diameter | [8 empty] | 24.3 |  |  |  |  | 33.4
| 24 | Piping Line Insulation | [8 empty] | N/A
BASIS | 25 | Type / Pressure Taps | [8 empty] | Flange Tapping |  |  |  |  | 2 TAPS
| 26 | Flow Rate Range | [7 empty] | Unit | 0 - 80 | [7 empty] | Kg/hr
| 27 | Differential Pressure @ Full scale | [8 empty] | 0 ~ 250 mbar
28
ORIFICE PLATE | 29 | Size and Flange Rating | [8 empty] | 1" |  |  |  |  | 300#
| 30 | Bore Diameter(d) | [8 empty] | 6.6132 mm(VTC)
| 31 | Diameter Ratio(beta=d/D) | [8 empty] | 0.198(VTC)
| 32 | Material | [8 empty] | 316 SS
| 33 | Thickness | [8 empty] | 3.2 mm (VTC)
| 34 | Ring Material and Type | [8 empty] | N/A |  |  |  |  | N/A
| 35 | Drain or Vent / Hole Size | [8 empty] | Drain/2mm(VTC)
| 36 | Actual Pressure Loss | [7 empty] | Unit | (VTC) | [7 empty] | mbar
| 37 | Applicable Standard | [8 empty] | ISO-5167/5168
ORIFICE FLANGES | 38 | Type | [8 empty] | Weld neck type
| 39 | Size, Rating and Facing | [8 empty] | 1" |  |  |  |  | 300# RF
| 40 | Flange Face Finish | [8 empty] | 125-250 AARH
| 41 | Flange Material | [8 empty] | ASTM A105
| 42 | Bolts and Nuts Material | [8 empty] | STUD BOLTS TO ASTM A193 GR.B7M,NUTS TO ASTM A194 GR.2HM
| 43 | Gasket Material | [8 empty] | Spiral Wound, 4.45mm,S.S 316 Winding/Graphite Filler,C.S. Outer& S.S 316L Inner Ring , ASME B16.20
| 44 | Jack Screw Material | [8 empty] | YES / ASTM A193-B7M
| 45 | Nipple Type for Press. Tap |  |  |  | Material |  |  |  | Qty. | TBE (L-150mm) /3000# /1/2" NPTM | [5 empty] | ASTM A106 GR.B |  | 2
| 46 | Pressure Taps Size |  |  |  |  | Orientation |  |  |  | 1/2" NPTF |  |  |  |  | 45º (Downward)
47
METER RUN | 48 | Upstream Length / Downstream Length | [7 empty] | Unit | 20D(VTA) |  |  |  | 5D(VTA) |  |  |  | mm
| 49 | Material / End Connection | [8 empty] | 316SS(NACE) |  |  |  |  | 1", 300# RF
| 50 | Straightening Vane | [8 empty] | N/A
PURCHASE | 51 | Manufacturer | [8 empty] | Will be finalized later
| 52 | Model | [8 empty] | Will be finalized later
| 53 | Requisition Number | [8 empty] | -
54
NOTES: 1-Orifice tag number, material, nominal diameter and bore diameter shall be permanently stamped on the orifice plate handle. 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable.