## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 11
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0010 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR LEVEL GAUGES نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 11
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0010 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-LG-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  |  | 1 | D-LG-2101 |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | C-100 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | TEG |  |  | TEG
| 6 | Upper Phase |  | Lower Phase |  |  |  | Liquid |  |  | Liquid
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 53.8/54.9 |  |  | 62/F.V. |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 62.08/63.6 |  |  | 5/148 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 0.01229 (vapor) and 7.17 (Liquid) |  |  | 0.01229 (vapor) and 7.17 (Liquid) |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 1069 |  |  | 1069 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | YES |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit | Transparent |  |  | 150-1050 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 1300 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 1040 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 3 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 2
| 27 | Body Material | [5 empty] | ASTM A105,NACE
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS,NACE
| 29 | Bonnet | [5 empty] | ASTM A105,NACE,(Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS,NACE
| 31 | Vessel Connection | Size |  | Rating |  |  | Standpipe connection 3" (3/4" LG Connection to the Standpipe) |  |  | 600#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES(VTC)
| 35 | Drain Connection | Size |  | Rating |  |  | 1/2" |  |  | 600#
| 36 |  | Type (Flange / NPT) |  |  |  |  | NPTF
| 37 | Vent Connection | Size |  | Rating |  |  | 1/2" |  |  | 600#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Drain Valve | [5 empty] | 1/2" NPTF, 600# Ball Valve (Body:ASTM A105 NACE/Trim:316 SS,NACE)
| 41 | Manufacturer | [5 empty] | Will be finalized later
| 42 | Model | [5 empty] | Will be finalized later
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | NO(VTC) |  |  | 230V AC
| 48 | Ex Certificate | [5 empty] | Eex d IIB T4(If Required)
| 49 | Ingress Protection | [5 empty] | IP65(If Required)
| 50 | Electrical connections | [5 empty] | M20 x 1.5(If Required)
51
PURCHASE | 52 | Manufacturer | [5 empty] | Will be finalized later
| 53 | Model | [5 empty] | Will be finalized later
| 54 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 2 | D-LG-2102 |  |  |  | 1
| 2 | Service | [5 empty] | C-100
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | C-100 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | HCB (WATER) |  |  | HCB (WATER)
| 6 | Upper Phase |  | Lower Phase |  |  |  | Liquid |  |  | Liquid
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 53.8/54.9 |  |  | 62/F.V. |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 62.08/63.6 |  |  | 5/148 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 0.49 |  |  | 0.49 |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 980.74 |  |  | 980.74 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | NO |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit | Transparent |  |  | 150-650 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 950 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 680 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 2 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 28 | Type | [5 empty] | Ball Check Offset Cock Valve
| 29 | Number Required | [5 empty] | 2
| 30 | Body Material | [5 empty] | ASTM A105 (VTC)
| 31 | Trim Material | [5 empty] | HARD FACE 316 SS
| 32 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 33 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 34 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 35 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 36 | Gauge Connection | Size |  |  |  |  | 3/4"
| 37 |  | Union(Yes/No) |  |  |  |  | YES
| 38 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 39 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 40 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 41 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 42 | Renewable Seats | [5 empty] | NA
| 43 | Manufacturer | [5 empty] | Will be selected later
| 44 | Model | [5 empty] | Will be selected later
| 45 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 46 | Mica Shield | [5 empty] | Yes
| 47 | Expansion Loop | [5 empty] | NA
| 48 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 49 | Jacket or Internal Tracer | [5 empty] | NA
| 50 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 51 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 52 | Ingress Protection | [5 empty] | IP65
| 53 | Scale | [5 empty] | Yes (mm)
| 54 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 55 | Manufacturer | [5 empty] | Will be finalized later
| 56 | Model | [5 empty] | Will be finalized later
| 57 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 3 | D-LG-2103 |  |  |  | 1
| 2 | Service | [5 empty] | V-120
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 2/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | V-120 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | HCB |  |  | HCB
| 6 | Upper Phase |  | Lower Phase |  |  |  | L |  |  | L
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 4.5 |  |  | 8 |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 73.5 |  |  | 120 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 0.3438 |  |  | 0.3438 |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 671.1 |  |  | 671.1 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | NO |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit |  |  |  | 200-400 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 600 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 320 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 1 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 1
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 52 | Manufacturer | [5 empty] | Will be finalized later
| 53 | Model | [5 empty] | Will be finalized later
| 54 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2104
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 4 | D-LG-2104 |  |  |  | 1
| 2 | Service | [5 empty] | V-120
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 2/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | V-120 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | TEG |  |  | TEG
| 6 | Upper Phase |  | Lower Phase |  |  |  | Liquid |  |  | Liquid
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 4.5 |  |  | 8/F.V. |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 73.63/74.53 |  |  | 5/120 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 5.33 |  |  | 5.33 |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 1017.63 |  |  | 1017.63 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | YES |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit | Transparent |  |  | 220-550 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 600 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 320 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 1 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 1
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 52 | Manufacturer | [5 empty] | Will be finalized later
| 53 | Model | [5 empty] | Will be finalized later
| 54 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2105
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 5 | D-LG-2105 |  |  |  | 1
| 2 | Service | [5 empty] | R-100
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | R-100 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | TEG |  |  | TEG
| 6 | Upper Phase |  | Lower Phase |  |  |  | Liquid |  |  | Liquid
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 0.3/0.6 |  |  | 4.1/F.V. |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 140/204 |  |  | 5/234 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 0.67 |  |  | 0.67 |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 981.71 |  |  | 981.71 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | YES |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit | Transparent |  |  | 800-960 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 600 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 320 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 1 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 2
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 52 | Manufacturer | [5 empty] | Will be finalized later
| 53 | Model | [5 empty] | Will be finalized later
| 54 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2106
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 6 | D-LG-2106 |  |  |  | 1
| 2 | Service | [5 empty] | V-130
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | V-130 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | TEG |  |  | TEG
| 6 | Upper Phase |  | Lower Phase |  |  |  | Liquid |  |  | Liquid
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 0.3/0.6 |  |  | 4.1/F.V. |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 140/204 |  |  | 5/234 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 0.67 |  |  | 0.67 |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 981.71 |  |  | 981.71 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | YES |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit | Transparent |  |  | 250-980 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 1300 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 1040 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 3 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 3
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 52 | Manufacturer | [5 empty] | Will be finalized later
| 53 | Model | [5 empty] | Will be finalized later
| 54 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2107
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 7 | D-LG-2107 |  |  |  | 1
| 2 | Service | [5 empty] | V-130
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | V-130 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | TEG |  |  | TEG
| 6 | Upper Phase |  | Lower Phase |  |  |  | Liquid |  |  | Liquid
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | 0.3/0.6 |  |  | 4.1/F.V. |  | barg
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | 140/204 |  |  | 5/234 |  | C
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | 0.67 |  |  | 0.67 |  | cp
| 10 | Upper Density |  | Lower Density |  |  | Unit | 981.71 |  |  | 981.71 |  | kg/m3
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | YES |  |  | YES
| 13 | Transparency |  | Measuring Range |  |  | Unit | Transparent |  |  | 250-980 |  | mm
14
GAUGE | 15 | Type | [5 empty] | Transparent
| 16 | Length Centre to Centre |  |  |  |  | Unit | 1300 |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 1040 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 3 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 3
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 52 | Manufacturer | [5 empty] | Will be finalized later
| 53 | Model | [5 empty] | Will be finalized later
| 54 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2108
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 8 | D-LG-2108 |  |  |  | 1
| 2 | Service | [5 empty] | TK-100
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 6/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TK-100 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 6 | Upper Phase |  | Lower Phase |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 10 | Upper Density |  | Lower Density |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 13 | Transparency |  | Measuring Range |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
14
GAUGE | 15 | Type | [5 empty] | Will be finalized later
| 16 | Length Centre to Centre |  |  |  |  | Unit | Will be finalized later |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 320 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 1 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 1
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 55 | Manufacturer | [5 empty] | Will be finalized later
| 56 | Model | [5 empty] | Will be finalized later
| 57 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LG-2109
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL GAUGES
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 11
9184 – 073 - 053 |  | BK | GCS | MF | 120 | IN | DS | 0010 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 9 | D-LG-2109 |  |  |  | 1
| 2 | Service | [5 empty] | TK-200
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 7/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TK-200 |  |  | NA
PROCESS CONDITIONS | 5 | Upper Fluid |  | Lower Fluid |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 6 | Upper Phase |  | Lower Phase |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 7 | Oper. Pressure: |  | Design Press.(Min/Max) |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 8 | Oper. Temperature: |  | Design Temp.(Min/Max) |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 9 | Upper Viscosity |  | Lower Viscosity |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 10 | Upper Density |  | Lower Density |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 11 | Corrosive Service |  | NACE Requirement |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 12 | Toxic Service |  | Solid in Suspension |  |  |  | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
| 13 | Transparency |  | Measuring Range |  |  | Unit | It will be finalized after receving Vendor data |  |  | It will be finalized after receving Vendor data
14
GAUGE | 15 | Type | [5 empty] | Will be finalized later
| 16 | Length Centre to Centre |  |  |  |  | Unit | Will be finalized later |  |  |  |  | mm
| 17 | Visible Range |  |  |  |  | Unit | 320 mm(VTC) |  |  |  |  | mm
| 18 | Sections Required |  | Section Glass Size |  |  |  | 1 x 9 (Note 1) |  |  | 320 mm (VTC)
| 19 | Connection Size & Type |  | Rating |  |  |  | 3/4", Flanged -RF |  |  | 600#
| 20 | Connection Layout | [5 empty] | Side - Side
| 21 | Body Material | [5 empty] | ASTM A105,NACE
| 22 | Glass Material | [5 empty] | Heat Resistant Borosilicat
| 23 | Wetted part Material | [5 empty] | SS316,NACE
| 24 | Gasket Material | [5 empty] | Asbestos free and capable of sealing under continuous pressure and temperature conditions of the gauge glass.
GAUGE COCKS | 25 | Type | [5 empty] | Ball Check Offset Cock Valve
| 26 | Number Required | [5 empty] | 1
| 27 | Body Material | [5 empty] | ASTM A105 (VTC)
| 28 | Trim Material | [5 empty] | HARD FACE 316 SS
| 29 | Bonnet | [5 empty] | ASTM A105 (Standard Bolted) VTC
| 30 | Ball Check | [5 empty] | YES , HARD FACE 316 SS
| 31 | Vessel Connection | Size |  | Rating |  |  | 2" |  |  | 800#RF
| 32 |  | Type (Flange / Union) |  |  |  |  | Flanged -RF
| 33 | Gauge Connection | Size |  |  |  |  | 3/4"
| 34 |  | Union(Yes/No) |  |  |  |  | YES
| 35 | Drain Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 36 |  | Type (Flange / NPT) |  |  |  |  | Flanged -RF
| 37 | Vent Connection | Size |  | Rating |  |  | 3/4" |  |  | 800#
| 38 |  | Type (Flange / NPT) |  |  |  |  | NPTF with Plug
| 39 | Renewable Seats | [5 empty] | NA
| 40 | Manufacturer | [5 empty] | Will be selected later
| 41 | Model | [5 empty] | Will be selected later
| 42 | Drain Valve | [5 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
OPTIONS | 43 | Mica Shield | [5 empty] | Yes
| 44 | Expansion Loop | [5 empty] | NA
| 45 | Frost Extension |  | Length |  |  |  | NA |  |  | NA
| 46 | Jacket or Internal Tracer | [5 empty] | NA
| 47 | Illuminator |  | Power Supply |  |  |  | YES |  |  | 220V AC
| 48 | Ex Certificate | [5 empty] | Eex d,IIB,T4
| 49 | Ingress Protection | [5 empty] | IP65
| 50 | Scale | [5 empty] | Yes (mm)
| 51 | Electrical connections | [5 empty] | M20 x 1.5
PURCHASE | 55 | Manufacturer | [5 empty] | Will be finalized later
| 56 | Model | [5 empty] | Will be finalized later
| 57 | Requisition Number
Note: 1- “9” refers to section size and “1” is quantity of section . 2-Gauge cock valve shall be of a quick acting, offset type and shall have bolted bonnets with Handwheels on Left or Right side of gauge and with bolted and Union gauge connection. 3-Each gauge shall be stamped with the maximum working pressure and temperature which is equal to or higher than the vessel design pressure and temperature ratings. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.