## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 17
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0011 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 17
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0011 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 |  | X | [7 empty] | 72
13 |  | X | [7 empty] | 73
14 |  | X | [7 empty] | 74
15 |  | X | [7 empty] | 75
16 |  | X | [7 empty] | 76
17 |  | X | [7 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-LIT-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 1 |  |  |  | D-LIT-2101 |  |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Equipment No. | [6 empty] | C-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 1069 |  |  |  |  | 1069 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 53.8/54.9 |  |  |  |  | 62/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 62.08/63.6 |  |  |  |  | 5/148 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 7.17 |  |  |  |  | 7.17 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | YES
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | HH |  |  | 150mm | [5 empty] | 1050mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 1219 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",600# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",600# RF
| 26 | C to C Dimension | [6 empty] | 1219 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 1219 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 2 |  |  |  | D-LIT-2102 |  |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Equipment No. | [6 empty] | C-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | HCB (WATER) |  |  |  |  | HCB (WATER)
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 980.74 |  |  |  |  | 980.74 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 53.8/54.9 |  |  |  |  | 62/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 62.08/63.6 |  |  |  |  | 5/148 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.49 |  |  |  |  | 0.79 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | YES
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | NO | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | NO | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | HH |  |  | 150mm | [5 empty] | 650mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 813 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",600# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",600# RF
| 26 | C to C Dimension | [6 empty] | 813 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 813 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 3 |  |  |  | D-LIT-2103 |  |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Equipment No. | [6 empty] | C-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 1069 |  |  |  |  | 1069 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 53.8/54.9 |  |  |  |  | 62/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 62.08/63.6 |  |  |  |  | 5/148 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 7.17 |  |  |  |  | 7.17 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | YES
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | H |  |  | NACE REQUIREMENT | HH |  |  | 950mm | [5 empty] | 1050mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",600# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",600# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2104
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 6 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 4 |  |  |  | D-LIT-2104 |  |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Equipment No. | [6 empty] | C-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 1069 |  |  |  |  | 1069 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 53.8/54.9 |  |  |  |  | 62/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 62.08/63.6 |  |  |  |  | 5/148 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 7.17 |  |  |  |  | 7.17 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | YES
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | L |  |  | 150mm | [5 empty] | 250mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",600# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",600# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2105
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 7 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 5 |  |  |  | D-LIT-2105 |  |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Equipment No. | [6 empty] | C-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | HCB (WATER) |  |  |  |  | HCB (WATER)
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 980.74 |  |  |  |  | 980.74 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 53.8/54.9 |  |  |  |  | 62/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 62.08/63.6 |  |  |  |  | 5/148 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.49 |  |  |  |  | 0.79 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | YES
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | NO | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | NO | [5 empty] | YES
| 16 | H |  |  | NACE REQUIREMENT | HH |  |  | 550mm | [5 empty] | 650mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",600# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",600# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2106
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 8 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 6 |  |  |  | D-LIT-2106 |  |  |  | 1
| 2 | Service | [6 empty] | C-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Equipment No. | [6 empty] | C-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | HCB (WATER) |  |  |  |  | HCB (WATER)
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 980.74 |  |  |  |  | 980.74 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 53.8/54.9 |  |  |  |  | 62/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 62.08/63.6 |  |  |  |  | 5/148 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.49 |  |  |  |  | 0.79 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | YES
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | NO | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | NO | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | L |  |  | 150mm | [5 empty] | 250mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",600# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",600# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2107
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 9 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 7 |  |  |  | D-LIT-2107 |  |  |  | 1
| 2 | Service | [6 empty] | V-120
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Equipment No. | [6 empty] | V-120
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | HCB |  |  |  |  | HCB
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 671.1 |  |  |  |  | 671.1 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 4.5 |  |  |  |  | 8 |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 73.5 |  |  |  |  | 120 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.3438 |  |  |  |  | 0.3438 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | NO | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | H |  |  | 200mm | [5 empty] | 400mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2108
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 10 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 8 |  |  |  | D-LIT-2108 |  |  |  | 1
| 2 | Service | [6 empty] | V-120
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Equipment No. | [6 empty] | V-120
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 1017.63 |  |  |  |  | 1017.63 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 4.5 |  |  |  |  | 8/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 73.63/74.53 |  |  |  |  | 5/120 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 5.33 |  |  |  |  | 5.33 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | H |  |  | NACE REQUIREMENT | HH |  |  | 465mm | [5 empty] | 550mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2109
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 11 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 9 |  |  |  | D-LIT-2109 |  |  |  | 1
| 2 | Service | [6 empty] | V-120
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Equipment No. | [6 empty] | V-120
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 1017.63 |  |  |  |  | 1017.63 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 4.5 |  |  |  |  | 8/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 73.63/74.53 |  |  |  |  | 5/120 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 5.33 |  |  |  |  | 5.33 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | L |  |  | 220mm | [5 empty] | 340mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2110
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 12 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 10 |  |  |  | D-LIT-2110 |  |  |  | 1
| 2 | Service | [6 empty] | V-120
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Equipment No. | [6 empty] | V-120
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 1017.63 |  |  |  |  | 1017.63 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 4.5 |  |  |  |  | 8/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 73.63/74.53 |  |  |  |  | 5/120 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 5.33 |  |  |  |  | 5.33 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | HH |  |  | 220mm | [5 empty] | 550mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2111
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 13 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 11 |  |  |  | D-LIT-2111 |  |  |  | 1
| 2 | Service | [6 empty] | R-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Equipment No. | [6 empty] | R-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 981.71 |  |  |  |  | 981.71 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 0.3/0.6 |  |  |  |  | 4.1/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 140/204 |  |  |  |  | 5/234 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.67 |  |  |  |  | 0.67 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | HH |  |  | 800mm | [5 empty] | 960mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2112
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 14 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 12 |  |  |  | D-LIT-2112 |  |  |  | 1
| 2 | Service | [6 empty] | R-100
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Equipment No. | [6 empty] | R-100
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 981.71 |  |  |  |  | 981.71 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 0.3/0.6 |  |  |  |  | 4.1/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 140/204 |  |  |  |  | 5/234 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.67 |  |  |  |  | 0.67 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | L |  |  | 800mm | [5 empty] | 900mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2114
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 15 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 14 |  |  |  | D-LIT-2114 |  |  |  | 1
| 2 | Service | [6 empty] | V-130
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Equipment No. | [6 empty] | V-130
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 981.71 |  |  |  |  | 981.71 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 0.3/0.6 |  |  |  |  | 4.1/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 140/204 |  |  |  |  | 5/234 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.67 |  |  |  |  | 0.67 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | HH |  |  | 250mm | [5 empty] | 980mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 813 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 813 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 813 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2115
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 16 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 15 |  |  |  | D-LIT-2115 |  |  |  | 1
| 2 | Service | [6 empty] | V-130
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Equipment No. | [6 empty] | V-130
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 981.71 |  |  |  |  | 981.71 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 0.3/0.6 |  |  |  |  | 4.1/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 140/204 |  |  |  |  | 5/234 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.67 |  |  |  |  | 0.67 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | H |  |  | NACE REQUIREMENT | HH |  |  | 850mm | [5 empty] | 980mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL
| 21 | Linkage Material | [6 empty] | Manufacture Standard
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" NPT(F)F Ball Valve (Body:ASTM A105 NACE/Trim:316L SS NACE)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | ASTM A105 NACE
| 32 | Gasket Material | [6 empty] | Spiral Wound, 4.45 mm Thick) THK.S.S 316 Winding /Graphite Filler, C.S. Outer& S.S 316L Inner Ring
| 33 | Bolt and Nut Material | [6 empty] | ASTM A 193-B7M/ASTM A 194 - 2HM
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIB T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Side mounted
| 46 | Housing Material | [6 empty] | Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left or Right hand(VTC)
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required.

## D-LIT-2116
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR LEVEL TRANSMITTERS
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات |  | رشته |  | نوع مدرک | سریال | نسخه | شماره صفحه: 17 از 17
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 |  | IN |  | DS | 0011 | V00
GENERAL DATA | 1 | Item Number |  |  | Tag Number |  | Quantity |  | 16 |  |  |  | D-LIT-2116 |  |  |  | 1
| 2 | Service | [6 empty] | V-130
| 3 | P & ID No. |  |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Equipment No. | [6 empty] | V-130
PROCESS CONDITIONS | 5 | Upper Fluid |  |  |  | Lower Fluid |  |  | TEG |  |  |  |  | TEG
| 6 | Upper Phase |  |  |  | Lower Phase |  |  | L |  |  |  |  | L
| 7 | Upper Phase Max Pressure (mbar) |  |  |  | Lower Phase Max Hieght |  | Unit
| 8 | Density / Sp.Gr. Upper |  |  |  | Density / Sp.Gr. Lower |  | Unit | 981.71 |  |  |  |  | 981.71 |  |  |  | kg/m3
| 9 | Oper. Press. |  |  |  | Design Press. |  | Unit | 0.3/0.6 |  |  |  |  | 4.1/F.V. |  |  |  | barg
| 10 | Oper. Temp. |  |  |  | Design Temp. |  | Unit | 140/204 |  |  |  |  | 5/234 |  |  |  | C
| 11 | Comply with NACE 0175 |  |  |  | Cold Service | [7 empty] | NO
| 12 | Viscosity Upper |  |  |  | Viscosity Lower |  | Unit | 0.67 |  |  |  |  | 0.67 |  |  |  | cp
| 13 | Solid in Suspension |  |  |  | WET GAS |  |  | YES | [5 empty] | NO
| 14 | TOXIC SERVICE |  |  | SUPERHEAT | SUPER HEAT |  |  | YES | [5 empty] | NO
| 15 | CORROSIVE SERVICE |  |  | NACE REQUIREMENT | NACE REQUIRMENT |  |  | YES | [5 empty] | YES
| 16 | LL |  |  | NACE REQUIREMENT | L |  |  | 250mm | [5 empty] | 350mm
DISPLACER | 17 | Type | [6 empty] | External Chamber
| 18 | Displacer Length / Hanger | [6 empty] | 356 mm / VTA
| 19 | Displacer Material | [6 empty] | 316 SS (NACE)
| 20 | Torque Tube or Spring Material | [6 empty] | INCONEL (VTC)
| 21 | Linkage Material | [6 empty] | Manufacture Standard (VTA)
22
HEAD / CHAMBER (CAGE) | 23 | Mounting Style | [6 empty] | SIDE and SIDE
| 24 | Vessel Connection (Size and Rating) |  |  |  | Upper |  |  | Flange, 2",300# RF
| 25 |  |  |  |  | Lower |  |  | Flange, 2",300# RF
| 26 | C to C Dimension | [6 empty] | 356 mm
| 27 | Head Connection | [6 empty] | FLANGE (Rotatable)
| 28 | Vent Connection | [6 empty] | Thread 3/4" NPT(F) X 3/4" plain half nipple with plug
| 29 | Drain Connection | [6 empty] | 3/4" 800# RF Ball Valve (ASTM A105/316L SS)
| 30 | Flange Face Finish | [6 empty] | 125-250 AARH
| 31 | Head / Chamber Material | [6 empty] | C.S (NOTE 5)
| 32 | Gasket Material | [6 empty] | SPIRAL WOUND / SS 316L / GRAPHITE; 4.5MM(0.18") THK.
| 33 | Bolt and Nut Material | [6 empty] | By Other
| 34 | Jacket Type & Fluid | [6 empty] | N/A
| 35 | Fin Extenction | [6 empty] | N/A
36
TRANSMITTER | 37 | Transmitter Type | [6 empty] | Electronic-Smart Type - HART
| 38 | Adjustable Range Min. / Max. | [6 empty] | 0 - 356 mm
| 39 | Calibration Range Min. / Max. | [6 empty] | 0 - 100%
| 40 | Output Signal |  |  |  | Power Supply |  |  | 4-20 mA (SMART) |  |  |  |  | 24VDC(LOOP POWERED)
| 41 | Enclosure Class |  |  |  | SIL Requirement/Level |  |  | Ex-ia IIC T4 |  |  |  |  | YES/SIL2
| 42 | Weather Protection | [6 empty] | IP65
| 43 | Electrical Connection | [6 empty] | M20x1.5
| 44 | Accuracy | [6 empty] | ±0.5 %
| 45 | Mounting | [6 empty] | Top mounted
| 46 | Housing Material | [6 empty] | Painted copper free Die Cast Aluminum
| 47 | LCD Indicator | [6 empty] | Yes
| 48 | Mounting Position | [6 empty] | Left hand
OPTIONS | 49 | Damping Adjustment | [6 empty] | Yes
| 50 | write protection | [6 empty] | Yes
PURCHASE | 51 | Manufacturer | [6 empty] | Will be selected later
| 52 | Requisition Number | [6 empty] | Will be selected later
53
54
NOTE: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Vendor to provide higher grade and proper material for fluid service if reqired,defined material is minimum requirement. 4-VTA: Vendor to advice. VTC: Vendor to confirm NA:Not Applicable NR: Not Required. 5-limitation for lower nozzle Connection impose to select higher C/C length.