## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW GAUGE
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 3
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0014 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR FLOW GAUGE نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW GAUGE
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 3
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0014 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 | [9 empty] | 64
5 | [9 empty] | 65
6 | [9 empty] | 66
7 | [9 empty] | 67
8 | [9 empty] | 68
9 | [9 empty] | 69
10 | [9 empty] | 70
11 | [9 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-FI-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW GAUGE
شماره پیمان: |  | پروژه | بسته کاری | صادر کننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 3
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 | IN | DS | 0014 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  |  |  |  | 1 | D-FI-2101 |  |  | 1
| 2 | Service | [8 empty] | FROM F100A TO E200
| 3 | P & ID No. |  | Page: | [6 empty] | BK-GCS-MF-120-PR-PI-0003 |  |  | 3/7
| 4 | Line No. / Equipment No. |  | Piping Class | [6 empty] | TEG-111-0013-AN07-1"-HI |  |  | AN07
PROCESS CONDITIONS | 5 | Fluid |  | Phase
| 6 | Flow: | Minimum | Normal | Maximum |  | Unit |  |  |  | 417.15 | 834.3 | 1001.16 |  | kg/h
| 7 | Pressure: | Minimum | Normal | Maximum |  | Unit |  |  |  | 3.5 | 3.8 | 4 |  | barg
| 8 | Temperature: | Minimum | Normal | Maximum |  | Unit |  |  |  | 70 | 74.53 | 80 |  | °C
| 9 | Design Pressure |  |  |  |  | Unit |  |  |  | F.V. / 8 |  |  |  | barg
| 10 | Design Temperature |  |  |  |  | Unit |  |  |  | 100 |  |  |  | °C
| 11 | Full Scale Flow |  |  |  |  | Unit |  |  |  | -
| 12 | Max.allowable pressure drop |  |  |  |  | Unit |  |  |  | -
| 13 | Operating Density |  |  |  |  | Unit |  |  |  | 901.1 |  |  |  | kg/m3
| 14 | Compressibility Factor (Z) | [8 empty] | 0.9551
| 15 | Molecular Weight |  | Cp / Cv | [6 empty] | 101.8 |  | 1.158 (L) and 1.058 (V)
| 16 | Vapor Pressure Pv |  |  |  |  | Unit |  |  |  | -
| 17 | Operating Viscosity |  |  |  |  | Unit |  |  |  | 0.01174 (L) / 5.545 (V) |  |  |  | cp
| 18 | Corrosive Service |  | Toxic Service | [6 empty] | YES |  | YES
| 19 | Solid in Suspension |  | NACE Requirement | [6 empty] | YES |  | YES
| 20 | Color or Transparency | [8 empty] | -
21
LINE | 22 | Pipe Size | [8 empty] | 1"
| 23 | Pipe Material |  | Pipe Insulation | [6 empty] | ASTM A106 Gr.B |  | PT (PAINT-NO INSULATION)
24
METERING ELEMENT & BODY | 25 | Mounting | [8 empty] | TUBING, VERTICAL
| 26 | Connection Size |  | Connection Type & Rating | [6 empty] | 1" |  | FLG(RF125 to 250 AARH),#600
| 27 | Connection Materials |  | Housing Material Finish | [6 empty] | ASTM A105 |  | Low Copper Die-Cast Aluminium
| 28 | Tube Material |  | Tube Size | [6 empty] | SS 316 (NACE) |  | VTA
| 29 | Float Material |  | Float Guide | [6 empty] | SS 316 (NACE) |  | SS 316 (NACE)
| 30 | Measuring Range | [8 empty] | 0~14.5 |  | 15 |  | kg/h
| 31 | Scale Factor |  | Meter Rated Accuracy | [6 empty] | Kg/h |  | ±2% FS
| 32 | Inlet Dir. |  | Outlet Dir | [6 empty] | BOTTOM |  | TOP
| 33 | Function | [8 empty] | Local Indication
| 34 | .Meter Scale : Length & Type |  | Glass type | [6 empty] | 125mm / METAL STRIP |  | Safety Glass
TRANSMITTER | 35 | Instrument Type |  | Model | [6 empty] | N/A |  | N/A
| 36 | Zero Adjustment |  | Span Adjustment | [6 empty] | N/A |  | N/A
| 37 | Accuracy |  | Repeatability | [6 empty] | N/A |  | N/A
| 38 | Integral Indicator |  | Scale Factor | [6 empty] | N/A |  | N/A
| 39 | RFI Protection |  | Write Protection | [6 empty] | N/A |  | N/A
| 40 | Power Supply |  | Power Consumption | [6 empty] | N/A |  | N/A
| 41 | Output Signal |  | Electrical Connection | [6 empty] | N/A |  | N/A
| 42 | Failure / Diagnostic Alarm | [8 empty] | N/A |  | N/A
| 43 | Housing Material |  | Mounting Type | [6 empty] | N/A |  | N/A
| 44 | Ex Certificate |  | Ingress Protection
45
ACCESSORIES | 46 | Needle Valve |  | Needle Valve Size & Material | [6 empty] | N/A |  | N/A
| 47 | Valve Location | [8 empty] | N/A
| 48 | Air Set |  | Purge Meter Tubing | [6 empty] | N/A |  | N/A
| 49 | Steam Jacket |  | Packing Material | [6 empty] | N/A |  | N/A
50
PURCHASE | 51 | Manufacturer | [8 empty] | Will be Selected Later
| 52 | Model | [8 empty] | Will be Selected Later
| 53 | Requisition Number | [8 empty] | Will be Selected Later
Note: The flow direction shall be clearly and permanently stamped on the meter body.