## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW TRANSMITTER
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 5
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0015 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR FLOW TRANSMITTER نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Mar.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW TRANSMITTER
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 5
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0015 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 | [9 empty] | 66
7 | [9 empty] | 67
8 | [9 empty] | 68
9 | [9 empty] | 69
10 | [9 empty] | 70
11 | [9 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-FIT-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW TRANSMITTER
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 5
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 | IN | DS | 0015 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 | D-FIT-2101 |  |  |  | 1
| 2 | Service | [5 empty] | E300 TO C100
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | TEG-111-0001-FN04-1"-HI |  |  |  | FN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | TEG |  |  |  | Liquid
| 6 | Flow Rate: | Minimum | Normal | Maximum |  | Unit | 387.5 | 775 |  |  | 930 | kg/h
| 7 | Operation Pressure: | Minimum | Normal | Maximum |  | Unit | 52 | 54.9 |  |  | 58 | barg
| 8 | Operation Temperature |  |  |  |  | Unit | 68 |  |  |  |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 62 |  |  |  |  | barg
| 10 | Design Temperature |  | Minimum | Maximum |  | Unit | 145 |  |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 7.924 |  |  |  |  | cp
| 12 | Solid in Suspension |  | Wet Gas |  |  |  | YES |  |  |  | NO
| 13 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  |  | YES
| 14 | Toxic Service |  | Superheat |  |  |  | YES |  |  |  | NO
15
TRANSMITTER | 16 | Instrument Type |  | Model |  |  |  | D/P CELL |  |  |  | Will be selected later
| 17 | Fllow Rate Range Min / Max |  |  |  |  | Unit | 0 - 1000 |  |  |  |  | Kg/ h
| 18 | Calibration Range |  |  |  |  | Unit | 0-250 |  |  |  |  | mbar
| 19 | Adjustable Range Min. / Max. |  |  |  |  | Unit | VTA |  |  |  |  | Barg
| 20 | Zero Adjustment |  | Span Adjustment |  |  |  | YES (Internal) |  |  |  | YES (Internal)
| 21 | Accuracy |  | Repeatability |  |  |  | ± 0.1% of full scale. |  |  |  | ± 0.25% of full scale (VTC)
| 22 | Integral Indicator |  | Scale Factor |  |  |  | YES |  |  |  | VTA
| 23 | RFI Protection |  | Write Protection |  |  |  | YES (VTC) |  |  |  | NO
| 24 | Power Supply |  | Power Consumption |  |  |  | 24 Vdc (2 wire), loop powered |  |  |  | VTA
| 25 | Output Signal |  | Electrical Connection |  |  |  | 4-20 mA, HART |  |  |  | ISO M20 x 1.5
| 26 | Failure / Diagnostic Alarm | [5 empty] | Self-Diagnostics
| 27 | Housing Material |  | Mounting Type |  |  |  | Painted Copper Free Die Cast Aluminum |  |  |  | YOKE (2" Pipe)
| 28 | Ex Certificate |  | Ingress Protection |  |  |  | EEx-i IIB T4 |  |  |  | IP65
| 29 | SIL Requirement/Level | [5 empty] | NO
SENSING & BODY | 30 | Element Type |  | Element Material |  |  |  | Diaphragm (VTC) |  |  |  | 316 SS
| 31 | Body Material |  | Body Rating |  |  |  | 316 SS |  |  |  | Mfr. Std.
| 32 | O-Rings Material |  | Bolts Material |  |  |  | Mfr. Std. |  |  |  | SS
| 33 | Instrument Connection | [5 empty] | 1/2" NPT Integral with 5-Way Valve Manifold
| 34 | Fill Fluid | [5 empty] | Silicone Oil
| 35 | Over range Protection |  | Maximum Static Pressure (barg) |  |  |  | YES (130% of maximum range) |  |  |  | VTA
| 36 | Ambient Temp. Effect |  | Operating Temp. Limits |  |  |  | kept to a minimum. |  |  |  | VTA
37
DIAPHRAGM SEAL | 38 | Type |  | Model Number |  |  |  | Clamped Diaphragm Seals(VTC) |  |  |  | Will be finalized later
| 39 | Process Connection |  | Instrument Connection |  |  |  | 2" Flanged type |  |  |  | 1/2" NPT(F)
| 40 | Connection Material |  | Connection Rating |  |  |  | SS316 RF |  |  |  | 600#
| 41 | Diaphragm Material | [5 empty] | 316 SS(NACE)
| 42 | Extended Length | [5 empty] | 316 SS(NACE)
| 43 | Bottom Housing Material | [5 empty] | 316 SS(NACE)
| 44 | Top Housing Material | [5 empty] | 316 SS(NACE)
| 45 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 46 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 47 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 48 | Capillary Length | [5 empty] | 3m
| 49 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 50 | Capillary Material | [5 empty] | 316 SS shielded by flexible stainless steel tubing with PVC cover (VTA)
51
MANIFOLD | 52 | Valve Type |  | Model |  |  |  | NA |  |  |  | NA
| 53 | Body Material |  | Trim Material |  |  |  | NA |  |  |  | NA
| 54 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  |  | NA
| 55 | Vent / Drain size |  | Valve Rating |  |  |  | NA |  |  |  | NA
| 56 | Packing Material | [5 empty] | NA
57
ACCESSORIES | 58 | Lightning Protection | [5 empty] | YES
| 59 | Mounting Brackets |  | Brackets Material |  |  |  | 2" Pipe Mounting Bracket |  |  |  | SS
| 60 | Name Plate | [5 empty] | YES (SS)
| 61 | Elec. integrally mounted indicator LCD |  | Tag Number |  |  |  | YES |  |  |  | YES
62
PURCHASE | 63 | Manufacturer | [5 empty] | Will be selected later
| 64 | Model | [5 empty] | Will be selected later
| 65 | Requisition Number | [5 empty] | Will be selected later
Note: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Square root extraction shall be performed in transmitter 4-Flowrate range shall be indicated in LCD indicator 5-Due to operation and design temperature supplier shall advice about Max operation temperature of transmitter 6-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard

## D-FIT-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW TRANSMITTER
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 4 از 5
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 | IN | DS | 0015 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 2 | D-FIT-2102 |  |  | 1
| 2 | Service | [5 empty] | WET GAS TO C100
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  | 1/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | GAS-111-0001-FN05-6"-PT |  |  | FN05
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | GAS |  |  | Vapor
| 6 | Flow Rate: | Minimum | Normal | Maximum |  | Unit | 8626.25 | 17252.5 |  | 20703 | kg/h
| 7 | Operation Pressure: | Minimum | Normal | Maximum |  | Unit | 50 | 53.9 |  | 58 | barg
| 8 | Operation Temperature |  |  |  |  | Unit | 60 |  |  |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | F.V. / 62 |  |  |  | barg
| 10 | Design Temperature |  | Minimum | Maximum |  | Unit | 148 |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.0141 |  |  |  | cp
| 12 | Solid in Suspension |  | Wet Gas |  |  |  | YES |  |  | YES
| 13 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 14 | Toxic Service |  | Superheat |  |  |  | YES |  |  | NO
15
TRANSMITTER | 16 | Instrument Type |  | Model |  |  |  | D/P CELL |  |  | Will be selected later
| 17 | Fllow Rate Range Min / Max |  |  |  |  | Unit | 0 - 2200 |  |  |  | Kg/ h
| 18 | Calibration Range |  |  |  |  | Unit | 0-250 |  |  |  | mbar
| 19 | Adjustable Range Min. / Max. |  |  |  |  | Unit | VTA |  |  |  | Barg
| 20 | Zero Adjustment |  | Span Adjustment |  |  |  | YES (Internal) |  |  | YES (Internal)
| 21 | Accuracy |  | Repeatability |  |  |  | ± 0.1% of full scale. |  |  | ± 0.25% of full scale (VTC)
| 22 | Integral Indicator |  | Scale Factor |  |  |  | YES |  |  | VTA
| 23 | RFI Protection |  | Write Protection |  |  |  | YES (VTC) |  |  | NO
| 24 | Power Supply |  | Power Consumption |  |  |  | 24 Vdc (2 wire), loop powered |  |  | VTA
| 25 | Output Signal |  | Electrical Connection |  |  |  | 4-20 mA, HART |  |  | ISO M20 x 1.5
| 26 | Failure / Diagnostic Alarm | [5 empty] | Self-Diagnostics
| 27 | Housing Material |  | Mounting Type |  |  |  | Painted Copper Free Die Cast Aluminum |  |  | YOKE (2" Pipe)
| 28 | Ex Certificate |  | Ingress Protection |  |  |  | EEx-i IIB T4 |  |  | IP65
| 29 | SIL Requirement/Level | [5 empty] | NO
SENSING & BODY | 30 | Element Type |  | Element Material |  |  |  | Diaphragm (VTC) |  |  | 316 SS (NACE)
| 31 | Body Material |  | Body Rating |  |  |  | 316 SS |  |  | Mfr. Std.
| 32 | O-Rings Material |  | Bolts Material |  |  |  | Mfr. Std. |  |  | SS
| 33 | Instrument Connection | [5 empty] | 1/2" NPT Integral with 5-Way Valve Manifold
| 34 | Fill Fluid | [5 empty] | Silicone Oil
| 35 | Over range Protection |  | Maximum Static Pressure (barg) |  |  |  | YES (130% of maximum range) |  |  | VTA
| 36 | Ambient Temp. Effect |  | Operating Temp. Limits |  |  |  | kept to a minimum. |  |  | VTA
37
DIAPHRAGM SEAL | 38 | Type |  | Model Number |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | Will be finalized later
| 39 | Process Connection |  | Instrument Connection |  |  |  | 2" Flanged type |  |  | 1/2" NPT(F)
| 40 | Connection Material |  | Connection Rating |  |  |  | SS316 RF |  |  | 600#
| 41 | Diaphragm Material | [5 empty] | 316 SS(NACE)
| 42 | Extended Length | [5 empty] | 316 SS(NACE)
| 43 | Bottom Housing Material | [5 empty] | 316 SS(NACE)
| 44 | Top Housing Material | [5 empty] | 316 SS(NACE)
| 45 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 46 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 47 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 48 | Capillary Length | [5 empty] | 3m
| 49 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 50 | Capillary Material | [5 empty] | 316 SS shielded by flexible stainless steel tubing with PVC cover (VTA)
51
MANIFOLD | 52 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 53 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 54 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 55 | Vent / Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 56 | Packing Material | [5 empty] | NA
57
ACCESSORIES | 58 | Lightning Protection | [5 empty] | YES
| 59 | Mounting Brackets |  | Brackets Material |  |  |  | 2" Pipe Mounting Bracket |  |  | SS
| 60 | Name Plate | [5 empty] | YES (SS)
| 61 | Elec. integrally mounted indicator LCD |  | Tag Number |  |  |  | YES |  |  | YES
62
PURCHASE | 63 | Manufacturer | [5 empty] | Will be selected later
| 64 | Model | [5 empty] | Will be selected later
| 65 | Requisition Number | [5 empty] | Will be selected later
Note: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Square root extraction shall be performed in transmitter 4-Flowrate range shall be indicated in LCD indicator 5-Due to operation and design temperature supplier shall advice about Max operation temperature of transmitter 6-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard

## D-FIT-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR FLOW TRANSMITTER
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده |  | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 5 از 5
9184 – 073 - 053 |  | BK | GCS | MF |  | 120 | IN | DS | 0015 | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 3 | D-FIT-2103 |  |  | 1
| 2 | Service | [5 empty] | STRIPPING GAS TO REBOILER
| 3 | P & ID No. |  | Page No. |  |  |  | BK-GCS-MF-120-PR-PI-0003 |  |  | 4/7
| 4 | Line No. / Equipment No. |  | Piping Class |  |  |  | FLG-111-0028-AN04-1"-PT |  |  | AN04
PROCESS CONDITIONS | 5 | Fluid |  | Phase |  |  |  | FUEL GAS |  |  | Gas
| 6 | Flow Rate: | Minimum | Normal | Maximum |  | Unit | 30 | 60 |  | 72 | kg/h
| 7 | Operation Pressure: | Minimum | Normal | Maximum |  | Unit | 4.2 | 4.9 |  | 5.2 | barg
| 8 | Operation Temperature |  |  |  |  | Unit | 48 |  |  |  | ˚C
| 9 | Design Pressure |  |  |  |  | Unit | 9 |  |  |  | barg
| 10 | Design Temperature |  | Minimum | Maximum |  | Unit | 85 |  |  |  | ˚C
| 11 | Operating Viscosity |  |  |  |  | Unit | 0.01147 |  |  |  | cp
| 12 | Solid in Suspension |  | Wet Gas |  |  |  | NO |  |  | NO
| 13 | Corrosive Service |  | NACE Requirement |  |  |  | YES |  |  | YES
| 14 | Toxic Service |  | Superheat |  |  |  | NO |  |  | NO
15
TRANSMITTER | 16 | Instrument Type |  | Model |  |  |  | D/P CELL |  |  | Will be selected later
| 17 | Fllow Rate Range Min / Max |  |  |  |  | Unit | 0-100 |  |  |  | Kg/ h
| 18 | Calibration Range |  |  |  |  | Unit | 0-250 |  |  |  | mbar
| 19 | Adjustable Range Min. / Max. |  |  |  |  | Unit | VTA |  |  |  | Barg
| 20 | Zero Adjustment |  | Span Adjustment |  |  |  | YES (Internal) |  |  | YES (Internal)
| 21 | Accuracy |  | Repeatability |  |  |  | ± 0.1% of full scale. |  |  | ± 0.25% of full scale (VTC)
| 22 | Integral Indicator |  | Scale Factor |  |  |  | YES |  |  | VTA
| 23 | RFI Protection |  | Write Protection |  |  |  | YES (VTC) |  |  | NO
| 24 | Power Supply |  | Power Consumption |  |  |  | 24 Vdc (2 wire), loop powered |  |  | VTA
| 25 | Output Signal |  | Electrical Connection |  |  |  | 4-20 mA, HART |  |  | ISO M20 x 1.5
| 26 | Failure / Diagnostic Alarm | [5 empty] | Self-Diagnostics
| 27 | Housing Material |  | Mounting Type |  |  |  | Painted Copper Free Die Cast Aluminum |  |  | YOKE (2" Pipe)
| 28 | Ex Certificate |  | Ingress Protection |  |  |  | EEx-i IIB T4 |  |  | IP65
| 29 | SIL Requirement/Level | [5 empty] | NO
SENSING & BODY | 30 | Element Type |  | Element Material |  |  |  | Diaphragm (VTC) |  |  | 316 SS
| 31 | Body Material |  | Body Rating |  |  |  | 316 SS |  |  | Mfr. Std.
| 32 | O-Rings Material |  | Bolts Material |  |  |  | Mfr. Std. |  |  | SS
| 33 | Instrument Connection | [5 empty] | 1/2" NPT Integral with 5-Way Valve Manifold
| 34 | Fill Fluid | [5 empty] | Silicone Oil
| 35 | Over range Protection |  | Maximum Static Pressure (barg) |  |  |  | YES (130% of maximum range) |  |  | VTA
| 36 | Ambient Temp. Effect |  | Operating Temp. Limits |  |  |  | kept to a minimum. |  |  | VTA
37
DIAPHRAGM SEAL | 38 | Type |  | Model Number |  |  |  | Clamped Diaphragm Seals(VTC) |  |  | Will be finalized later
| 39 | Process Connection |  | Instrument Connection |  |  |  | 2" Flanged type |  |  | 1/2" NPT(F)
| 40 | Connection Material |  | Connection Rating |  |  |  | SS316 RF |  |  | 300#
| 41 | Diaphragm Material | [5 empty] | 316 SS(NACE)
| 42 | Extended Length | [5 empty] | 316 SS(NACE)
| 43 | Bottom Housing Material | [5 empty] | 316 SS(NACE)
| 44 | Top Housing Material | [5 empty] | 316 SS(NACE)
| 45 | Flushing Connection | [5 empty] | 1/4" NPTM(VTC)
| 46 | Fill Connection | [5 empty] | 1/4" NPTF(VTC)
| 47 | Fill Fluid | [5 empty] | Silicone oil (VTC)
| 48 | Capillary Length | [5 empty] | 3m
| 49 | Capillary Bleeder | [5 empty] | YES/1/4" NPTF(VTC)
| 50 | Capillary Material | [5 empty] | 316 SS shielded by flexible stainless steel tubing with PVC cover (VTA)
51
MANIFOLD | 52 | Valve Type |  | Model |  |  |  | NA |  |  | NA
| 53 | Body Material |  | Trim Material |  |  |  | NA |  |  | NA
| 54 | Process Connection |  | Instrument Connection |  |  |  | NA |  |  | NA
| 55 | Vent / Drain size |  | Valve Rating |  |  |  | NA |  |  | NA
| 56 | Packing Material | [5 empty] | NA
57
ACCESSORIES | 58 | Lightning Protection | [5 empty] | YES
| 59 | Mounting Brackets |  | Brackets Material |  |  |  | 2" Pipe Mounting Bracket |  |  | SS
| 60 | Name Plate | [5 empty] | YES (SS)
| 61 | Elec. integrally mounted indicator LCD |  | Tag Number |  |  |  | YES |  |  | YES
62
PURCHASE | 63 | Manufacturer | [5 empty] | Will be selected later
| 64 | Model | [5 empty] | Will be selected later
| 65 | Requisition Number | [5 empty] | Will be selected later
Note: 1- Engraved stainless steel corrosion resistant tag nameplate is required for transmitter. 2-Transmitter shall be provided with ground lug 3-Square root extraction shall be performed in transmitter 4-Flowrate range shall be indicated in LCD indicator 5-Due to operation and design temperature supplier shall advice about Max operation temperature of transmitter 6-All the wetted parts in sour service shall be in accordance with NACE MR-01-75/ISO 15156 standard