## Cover
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
CAUSE AND EFFECT DIAGRAM FOR GAS DEHYDRATION PACKAGE
شماره پیمان: | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 1 از 3
9184 – 073 - 053 | BK | GCS | MF | 120 | PR | CE | 0001 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
CAUSE AND EFFECT DIAGRAM FOR GAS DEHYDRATION PACKAGE نگهداشت و افزایش تولید میدان نفتی بینک

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
CAUSE AND EFFECT DIAGRAM FOR GAS DEHYDRATION PACKAGE
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 2 از 3
9184 – 073 - 053 |  | BK | GCS | MF | 120 | PR | CE | 0001 | V00
REVISION RECORD SHEET
Page | V00 | V01 | V02 | V03 | V04 |  | Page | V00 | V01 | V02 | V03 | V04
1 | X | [5 empty] | 61
2 | X | [5 empty] | 62
3 | X | [5 empty] | 63
4 | [6 empty] | 64
5 | [6 empty] | 65
6 | [6 empty] | 66
7 | [6 empty] | 67
8 | [6 empty] | 68
9 | [6 empty] | 69
10 | [6 empty] | 70
11 | [6 empty] | 71
12 | [6 empty] | 72
13 | [6 empty] | 73
14 | [6 empty] | 74
15 | [6 empty] | 75
16 | [6 empty] | 76
17 | [6 empty] | 77
18 | [6 empty] | 78
19 | [6 empty] | 79
20 | [6 empty] | 80
21 | [6 empty] | 81
22 | [6 empty] | 82
23 | [6 empty] | 83
24 | [6 empty] | 84
25 | [6 empty] | 85
26 | [6 empty] | 86
27 | [6 empty] | 87
28 | [6 empty] | 88
29 | [6 empty] | 89
30 | [6 empty] | 90
31 | [6 empty] | 91
32 | [6 empty] | 92
33 | [6 empty] | 93
34 | [6 empty] | 94
35 | [6 empty] | 95
36 | [6 empty] | 96
37 | [6 empty] | 97
38 | [6 empty] | 98
39 | [6 empty] | 99
40 | [6 empty] | 100
41 | [6 empty] | 101
42 | [6 empty] | 102
43 | [6 empty] | 103
44 | [6 empty] | 104
45 | [6 empty] | 105
46 | [6 empty] | 106
47 | [6 empty] | 107
48 | [6 empty] | 108
49 | [6 empty] | 109
50 | [6 empty] | 110
51 | [6 empty] | 111
52 | [6 empty] | 112
53 | [6 empty] | 113
54 | [6 empty] | 114
55 | [6 empty] | 115
56 | [6 empty] | 116
57 | [6 empty] | 117
58 | [6 empty] | 118
59 | [6 empty] | 119
60 | [6 empty] | 120

## H-8201
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
CAUSE AND EFFECT DIAGRAM FOR GAS DEHYDRATION PACKAGE
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک |  |  |  | سریال |  |  |  | نسخه |  |  |  |  | شماره صفحه: 3 از 3
9184 – 073 - 053 |  |  | BK | GCS | MF | 120 | PR | CE |  |  |  | 0001 |  |  |  | V00
ACTION LEGEND A = ACTIVE O = OPEN D = DEACTIVE C = CLOSE AS = AUTO START SD = SHUTDOWN ABBREVIATION BMS = BURNER MANAGEMENT SYSTEM | [6 empty] | EFFECT | NOTE
[8 empty] | SERVICE | LEAN GLYCOL CIRCULATION PUMP SHUTDOWN | GLYCOL PUMP FOR ANTI FOAM INJECTION PACKAGE | GLYCOL PUMP FOR PH CONTROL INJECTION PACKAGE | ON-OFF VALVE OF RICH GLYCOL FROM CONTACTOR | ON-OFF VALVE OF WET GAS TO CONTACTOR | ON-OFF VALVE OF CONDENSATE FROM CONTACTOR | ON-OFF VALVE OF GLYCOL TO STILL COLUMN | REBOILER SHUTDOWN | REBOILER MAIN BURNER SHUTDOWN | FUEL GAS TO BURNER BLOCK VALVE (A) | FUEL GAS TO BURNER BLOCK VALVE (B) | FUEL GAS TO BURNER BLEED VALVE (C) | FUEL GAS TO PILOT BLOCK VALVE (A) | FUEL GAS TO PILOT BLOCK VALVE (B) | FUEL GAS TO PILOT BLEED VALVE (C) | AUTO START OTHER LEAN GLYCOL CIRCULATION PUMP | AUTO START OTHER GLYCOL PUMP FOR ANTI FOAM INJECTION PACKAGE | AUTO START OTHER GLYCOL PUMP FOR PH CONTROL INJECTION PACKAGE
[8 empty] | TAG NO. | P-100 A/B | P-200 A/B | P-300 A/B | ESDV-2101 | ESDV-2142 | ESDV-2102 | ESDV-2103 | XA-2107 | XA-2105 | ESDV-2104A | ESDV-2104B | ESDV-2104C | ESDV-2105A | ESDV-2105B | ESDV-2105C | MCC (P100A/B) | MCC (P200A/B) | MCC (P300A/B)
[8 empty] | NO. | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18
CAUSE | [7 empty] | REV | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00 | 00
REV | NO. | TAG NO. | SERVICE | P&ID NO. | INTERLOCK | SIL | NOTE
00 | 1 | TAHH-2102 | LEAN GLYCOL TEMPERATURE HIGH HIGH |  | I-3 | bar: 1 to 3
00 | 2 | LAHH-2103 | RICH GLYCOL LEVEL HIGH HIGH IN CONTACTOR |  | I-3 | bar: 1 to 3
00 | 3 | LALL-2102 | RICH GLYCOL LEVEL LOW LOW IN CONTACTOR |  | I-5 | bar: 4
00 | 4 | LAHH-2105 | CONDENSATE LEVEL HIGH HIGH IN CONTACTOR |  | I-6 | bar: 5
00 | 5 | LALL-2106 | CONDENSATE LEVEL LOW LOW IN CONTACTOR |  | I-7 | bar: 6
00 | 6 | LAHH-2108 | GLYCOL LEVEL HIGH HIGH IN FLASH DRUM |  | I-5 | bar: 4
00 | 7 | LALL-2109 | GLYCOL LEVEL LOW LOW IN FLASH DRUM |  | I-8 | bar: 7
00 | 8 | PAHH-2102 | REBOILER PRESSURE HIGH HIGH |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 9 | LALL-2112 | GLYCOL LEVEL LOW LOW IN REBOILER |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 10 | TAHH-2108 | STACK TEMPERATURE HIGH HIGH |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 11 | TAHH-2106 | REBOILER HIGH HIGH TEMPERATURE |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 12 | PAHH-2104 | FUEL GAS TO PILOT HIGH HIGH PRESSURE |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 13 | PALL-2104 | FUEL GAS TO PILOT LOW LOW PRESSURE |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 14 | BALL-2101 | PILOT FLAME FAILURE |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 15 | HS-2101 | MANUAL ACTIVATION FROM BMS FRONT PANEL(REBOILER EMERGENCY S.DOWN) |  | I-1 |  |  |  | 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 16 | PAHH-2103 | FLUE GAS TO MAIN BURNER PRESSURE HIGH HIGH |  | I-2 |  |  |  | 9: SD; 10: C; 11: C; 12: O
00 | 17 | PALL-2103 | FLUE GAS TO MAIN BURNER PRESSURE LOW LOW |  | I-2 |  |  |  | 9: SD; 10: C; 11: C; 12: O
00 | 18 | BALL-2102 | MAIN BURNER FLAME FAILURE |  | I-2 |  |  |  | 9: SD; 10: C; 11: C; 12: O
00 | 19 | LAHH-2115 | GLYCOL LEVEL HIGH HIGH IN SURGE DRUM |  | I-1 / I-5 |  |  |  | 4: C; 8: SD; 9: SD; 10: C; 11: C; 12: O; 13: C; 14: C; 15: O
00 | 20 | LALL-2116 | GLYCOL LEVEL LOW LOW IN SURGE DRUM |  | I-4 | bar: 1 to 3
00 | 21 | - | SWITCH LEAN GLYCOL CIRCULATION PUMP FROM UCP |  | I-9 | bar: 16
00 | 22 | - | SWITCH GLYCOL PUMP FOR ANTI FOAM INJECTION PACKAGE FROM UCP |  | I-10 | bar: 17
00 | 23 | - | SWITCH GLYCOL PUMP FOR PH CONTROL INJECTION PACKAGE FROM UCP |  | I-11 | bar: 18