## Cover
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08)
ALARM & TRIP SET POINT LIST
شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 4
9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | PR | LI | 0002 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
ALARM & TRIP SET POINT LIST نگهداشت و افزایش تولید میدان نفتی بینک
V00 |  | Apr.2025 |  | IFI |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08)
ALARM & TRIP SET POINT LIST
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 4
9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | PR | LI | 0002 |  | V00
REVISION RECORD SHEET
Page | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 | * | [7 empty] | 65
2 | * | [7 empty] | 66
3 | * | [7 empty] | 67
4 | * | [7 empty] | 68
5 | [8 empty] | 69
6 | [8 empty] | 70
7 | [8 empty] | 71
8 | [8 empty] | 72
9 | [8 empty] | 73
10 | [8 empty] | 74
11 | [8 empty] | 75
12 | [8 empty] | 76
13 | [8 empty] | 77
14 | [8 empty] | 78
15 | [8 empty] | 79
16 | [8 empty] | 80
17 | [8 empty] | 81
18 | [8 empty] | 82
19 | [8 empty] | 83
20 | [8 empty] | 84
21 | [8 empty] | 85
22 | [8 empty] | 86
23 | [8 empty] | 87
24 | [8 empty] | 88
25 | [8 empty] | 89
26 | [8 empty] | 90
27 | [8 empty] | 91
28 | [8 empty] | 92
29 | [8 empty] | 93
30 | [8 empty] | 94
31 | [8 empty] | 95
32 | [8 empty] | 96
33 | [8 empty] | 97
34 | [8 empty] | 98
35 | [8 empty] | 99
36 | [8 empty] | 100
37 | [8 empty] | 101
38 | [8 empty] | 102
39 | [8 empty] | 103
40 | [8 empty] | 104
41 | [8 empty] | 105
42 | [8 empty] | 106
43 | [8 empty] | 107
44 | [8 empty] | 108
45 | [8 empty] | 109
46 | [8 empty] | 110
47 | [8 empty] | 111
48 | [8 empty] | 112
49 | [8 empty] | 113
50 | [8 empty] | 114
51 | [8 empty] | 115
52 | [8 empty] | 116
53 | [8 empty] | 117
54 | [8 empty] | 118
55 | [8 empty] | 119
56 | [8 empty] | 120
57 | [8 empty] | 121
58 | [8 empty] | 122
59 | [8 empty] | 123
60 | [8 empty] | 124
61 | [8 empty] | 125
62 | [8 empty] | 126
63 | [8 empty] | 127
64 | [8 empty] | 128

## H-8202
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض
خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08)
ALARM & TRIP SET POINT LIST
شماره پیمان: |  | پروژه | بسته کاری | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال | نسخه | شماره صفحه: 3 از 4
9184 – 073 - 053 |  | BK | GCS | MF | 120 | PR | LI | 0002 | V00
No. | Tag | Type | Description | I/O Type | Signal Type | operating condition |  | Calibration Range | Alarm & Set Point |  |  |  | Unit | Remark
[6 empty] | Summer | Winter |  | LL | L | H | HH
1 | TIT-2101 | Temperature Indicator Transmitter | Wet Gas to Dehydration Column Temperature Indicator Transmitter | AI | 4-20mA | 59.89 | 60 | 0-100 |  |  | 65 |  | ˚C
2 | FIT-2102 | Flow Indicator Transmitter | Wet Gas to Dehydration Column Flow Indicator Transmitter | AI | 4-20mA | 17252.5 | 15170.9 | 0 - 2200 |  |  | 18977 (s) 16678 (w) |  | kg/h
3 | LIT-2102 | Level Indicator Transmitter | Level Indicator Transmitter of Condensate at Dehydration Column | AI | 4-20mA | 400 | 400 | 0-100% |  | 250 | 550 |  | mm
4 | LIT-2103 | Level Indicator Transmitter | Level Indicator Transmitter of TEG at Dehydration Column | AI | 4-20mA | 600 | 600 | 0-100% |  |  |  | 1050 | mm
5 | LIT-2101 | Level Indicator Transmitter | Level Indicator Transmitter of TEG at Dehydration Column | AI | 4-20mA | 600 | 600 | 0-100% |  | 250 | 950 |  | mm
6 | LIT-2106 | Level Indicator Transmitter | Level Indicator Transmitter of Condensate at Dehydration Column | AI | 4-20mA | 400 | 400 | 0-100% | 150 |  |  |  | mm
7 | LIT-2105 | Level Indicator Transmitter | Level Indicator Transmitter of Condensate at Dehydration Column | AI | 4-20mA | 400 | 400 | 0-100% |  |  |  | 650 | mm
8 | LIT-2104 | Level Indicator Transmitter | Level Indicator Transmitter of TEG at Dehydration Column | AI | 4-20mA | 600 | 600 | 0-100% | 150 |  |  |  | mm
9 | TIT-2102 | Temperature Indicator Transmitter | Lean TEG to Dehydration Column Temperature Indicator Transmitter | AI | 4-20mA | 68 | 68 | 0-100 |  |  | 73 | 78 | ˚C
10 | FIT-2101 | Flow Indicator Transmitter | Lean TEG to Dehydration Column Flow Transmitter | AI | 4-20mA | 775 | 775 | 0-1000 |  | 300 | 852 |  | kg/h
11 | PDIT-2102 | Pressure Differential Indicator Transmitter | Pressure Differential Indicator Transmitter of Structured Packing | AI | 4-20mA | 0.01 | 0.01 | 0-0.2 |  |  | 0.1 |  | bar | (1)
12 | AIT-2101 | Analyzer Indicator Transmitter | H2O Analyzer Indicator Transmitter for Dry Gas | AI | 4-20mA | 240 | 240 | 1-1000 |  |  | 450 |  | ppmv
13 | PDIT-2101 | Pressure Differential Indicator Transmitter | Pressure Differential Indicator Transmitter of Wire Mesh | AI | 4-20mA | 0.01 | 0.01 | 0-0.2 |  |  | 0.1 |  | bar | (1)
14 | LIT-2107 | Level Indicator Transmitter | Level Indicator Transmitter of Hydrocarbon at Flash Drum | AI | 4-20mA | 300 | 300 | 0-100% |  | 200 | 400 |  | mm
15 | LIT-2108 | Level Indicator Transmitter | Level Indicator Transmitter of TEG at Flash Drum | AI | 4-20mA | 390 | 390 | 0-100% |  |  |  | 550 | mm
16 | LIT-2109 | Level Indicator Transmitter | Level Indicator Transmitter of TEG at Flash Drum | AI | 4-20mA | 390 | 390 | 0-100% | 220 |  |  |  | mm
17 | LIT-2110 | Level Indicator Transmitter | Level Indicator Transmitter of TEG at Flash Drum | AI | 4-20mA | 390 | 390 | 0-100% |  | 340 | 465 |  | mm
18 | TIT-2105 | Temperature Indicator Transmitter | Temperature Indicator Transmitter of Flash Drum | AI | 4-20mA | 74.53 | 73.63 | 0-100 |  | 60 | 85 |  | ˚C
19 | TIT-2108 | Temperature Indicator Transmitter | Temperature Indicator Transmitter of Flue Gas | AI | 4-20mA | 450-550 | 450-550 | 0-800 |  |  |  | 600 | ˚C
20 | TIT-2107 | Temperature Indicator Transmitter | Temperature Indicator Transmitter of Outlet Gas from Still Column | AI | 4-20mA | 86.16 | 86.85 | 0-120 |  | 80 | 100 |  | ˚C
21 | PIT-2103 | Pressure Indicator Transmitter | Pressure Indicator Transmitter of Fuel Gas to Burner | AI | 4-20mA | 1 | 1 | 0-2 | 0.05 | 0.09 | 1.5 | 1.7 | barg | (2)
22 | PIT-2104 | Pressure Indicator Transmitter | Pressure Indicator Transmitter of Fuel Gas to Pilot | AI | 4-20mA | 0.5 | 0.5 | 0-1 | 0.2 | 0.3 | 0.7 | 0.8 | barg | (2)
23 | TIT-2109 | Temperature Indicator Transmitter | Reboiler and Surge Drum Temperature Indicator Transmitter | AI | 4-20mA | 204 | 204 | 0-300 |  | 140 | 207 |  | ˚C
24 | TIT-2106 | Temperature Indicator Transmitter | Reboiler and Surge Drum Temperature Indicator Transmitter | AI | 4-20mA | 204 | 204 | 0-300 |  |  |  | 210 | ˚C
25 | PIT-2102 | Pressure Indicator Transmitter | Reboiler and Surge Drum Pressure Indicator Transmitter | AI | 4-20mA | 0.3 | 0.3 | 0-2.5 |  |  |  | 1.4 | barg
26 | LIT-2111 | Level Indicator Transmitter | Reboiler Level Indicator Transmitter | AI | 4-20mA | 945 | 945 | 0-100% |  | 900 | 960 |  | mm
27 | FIT-2103 | Flow Indicator Transmitter | Stripping Gas to Surge Drum Flow Transmitter | AI | 4-20mA | 60 | 45 | 0-100 |  | 20 | 80 |  | kg/h
28 | LIT-2112 | Level Indicator Transmitter | Reboiler Level Indicator Transmitter | AI | 4-20mA | 945 | 945 | 0-100% | 800 |  |  |  | mm
29 | LIT-2114 | Level Indicator Transmitter | Level Indicator Transmitter of Surge Section | AI | 4-20mA | 750 |  | 0-100% |  | 350 | 850 |  | mm
30 | LIT-2115 | Level Indicator Transmitter | Level Indicator Transmitter of Surge Section | AI | 4-20mA | 750 |  | 0-100% |  |  |  | 980 | mm
31 | LIT-2116 | Level Indicator Transmitter | Level Indicator Transmitter of Surge Section | AI | 4-20mA | 750 |  | 0-100% | 250 |  |  |  | mm
NOTES: (1) Will be finalized after receiving internal vendor data. (2) Will be finalized after receiving burner vendor data.