## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 10
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0001 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR CONTROL VALVES نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Apr.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 10
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0001 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 | [9 empty] | 71
12 | [9 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-FCV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 3 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 1 |  | D-FCV-2101 | [5 empty] | 1
| 2 | Service | [9 empty] | FROM E-300 TO P-100-A/B
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | TEG-111-0002-FN04-1"-HI | [6 empty] | FN04
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | TEG |  |  | Liquid
| 6 | [10 empty] | Min. Flow |  | Normal. Flow (4) |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | 38.75 |  | 116.25 |  |  |  |  | 620 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [11 empty] | 54.9 | [9 empty] | barg
| 9 | Outlet Pressure | [11 empty] | 0.2 | [9 empty] | barg
| 10 | Inlet Temperature | [11 empty] | 68 | [9 empty] | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 147.91 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 1045.15 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 7.924 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 0.1275 |  |  |  |  | - |  |  |  |  | barg
| 15 | Flash | [9 empty] | - |  | - |  |  |  |  | -
| 16 | Calculated Cv / Travel | [9 empty] | - |  | - |  |  |  |  | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.0221 |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.045 |  |  |  |  | -
| 20 | Critical Pres. Pc (Barg) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 13.96 |  | 453.1 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | NO |  | YES |  |  |  |  | NO
| 22 | NACE Requirement | [9 empty] | NO
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec | [10 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 600# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #600 |  |  | 1" #600 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Flow Tends To Open(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) /Bellows Seal | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(5) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(5) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(5) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(5) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | NO
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-NNF (Normally No Flow) 5-Trim number 12 same as API 602. 6:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-LCV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 4 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 2 |  | D-LCV-2101 | [5 empty] | 1
| 2 | Service | [9 empty] | FROM C-100 TO E-100
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | TEG-111-0002-FN07-1"-PT | [6 empty] | FN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | TEG |  |  | Liquid
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | 300 |  | 849.5 |  |  |  |  | 934.45 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [11 empty] | 53.8 ̴ 54.9 | [9 empty] | barg
| 9 | Outlet Pressure | [11 empty] | 5.5 | [9 empty] | barg
| 10 | Inlet Temperature | [11 empty] | 62.08 ̴ 63.6 | [9 empty] | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 98.24 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 1072 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 7.077 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 51.68 |  |  |  |  | - |  |  |  |  | barg
| 15 | Flash | [9 empty] | - |  | - |  |  |  |  | -
| 16 | Calculated Cv / Travel | [9 empty] | - |  | - |  |  |  |  | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.1811 / 0.2146 |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.063 |  |  |  |  | -
| 20 | Critical Pres. Pc (Barg) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 35.52 |  | 428.2 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | YES |  | YES |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec | [10 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 600# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 (NACE) | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1 " #600 |  |  | 1" #600 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note4) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-Trim number 12 same as API 602. 5:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-LCV-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 5 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 3 |  | D-LCV-2102 | [5 empty] | 1
| 2 | Service | [9 empty] | FROM C-100 TO DEHYDRATION DRIAN LINE
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 1/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | HCB-111-0003-FN07-1"-PT | [6 empty] | FN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | HCB |  |  | Liquid
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | min. |  | 5.9 |  |  |  |  | 10 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [9 empty] | 48.51 |  | 53.9 |  |  |  |  | 59.29 |  |  |  |  | barg
| 9 | Outlet Pressure | [9 empty] | 3.5 |  | 3.5 |  |  |  |  | 3.5 |  |  |  |  | barg
| 10 | Inlet Temperature | [9 empty] | 48 |  | 59.89 ̴ 60 |  |  |  |  | 72 |  |  |  |  | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 18.04 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 980 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 0.49 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 53.9 |  |  |  |  | - |  |  |  |  | barg
| 15 | Flash | [9 empty] | - |  | - |  |  |  |  | -
| 16 | Calculated Cv / Travel | [9 empty] | - |  | - |  |  |  |  | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.0933 (vapor phase) |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.012 |  |  |  |  | -
| 20 | Critical Pres. Pc (Barg) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 222.4 |  | 373.9 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | YES |  | YES |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec | [10 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 600# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #600 |  |  | 1" #600 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note4) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-Trim number 12 same as API 602. 5:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-LCV-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 6 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 4 |  | D-LCV-2103 | [5 empty] | 1
| 2 | Service | [9 empty] | FROM V-120 TO HC CLOSED DRAIN HEADER
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | HCB-111-0001-FN07-1"-PT | [6 empty] | FN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | HCB |  |  | V/L
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | min. |  | 28.02 |  |  |  |  | 33.624 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [9 empty] | 4.05 |  | 4.5 |  |  |  |  | 4.95 |  |  |  |  | barg
| 9 | Outlet Pressure | [9 empty] | 3.5 |  | 3.5 |  |  |  |  | 3.5 |  |  |  |  | barg
| 10 | Inlet Temperature | [9 empty] | 47.912 |  | 59.89 |  |  |  |  | 71.868 |  |  |  |  | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 101.9 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 661 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 19.4 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 4.5 |  |  |  |  | - |  |  |  |  | barg
| 15 | Flash | [9 empty] | - |  | - |  |  |  |  | -
| 16 | Calculated Cv / Travel | [9 empty] | - |  | - |  |  |  |  | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.01765 |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.058 |  |  |  |  | -
| 20 | Critical Pres. Pc (Barg) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 31.34 |  | 430.6 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | YES |  | YES |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec |  |  |  | IH | [6 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 600# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 (NACE) | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #600 |  |  | 1" #600 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note5) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | THREE-WAY | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | LCV-2103 | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | SS 316 | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | 24Vdc | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | M20*1.5 | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | YES | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | Zone 2 EX ia IIB T4 |  |  | IP65 |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | VTA | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-NNF (Normally No Flow) 5-Trim number 12 same as API 602. 6:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-PCV-2101A
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 7 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 5 |  | D-PCV-2101A | [5 empty] | 1
| 2 | Service | [9 empty] | V-120 TO LP FLARE
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | GAS-111-0005-AN07-1"-PP | [6 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | GAS |  |  | Gas
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | 5.25 |  | 10.5/15.2 |  |  |  |  | 18.24 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [9 empty] | 4.5 |  | 4.5 |  |  |  |  | 4.95 |  |  |  |  | barg
| 9 | Outlet Pressure | [9 empty] | 4.5 |  | 4.5 |  |  |  |  | 4.5 |  |  |  |  | barg
| 10 | Inlet Temperature | [9 empty] | 58.904 |  | 73.63/74.53 |  |  |  |  | 89.436 |  |  |  |  | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 33.62 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 5.79/6.59 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 0.01254 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 4.5 |  |  |  |  | - |  |  |  |  | barg
| 15 | Flash | [9 empty] | - | [6 empty] | -
| 16 | Calculated Cv / Travel | [9 empty] | - | [6 empty] | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.9678 |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.189 |  |  |  |  | -
| 20 | Critical Pres. Pc (Barg) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 104.7 |  | 86.71 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | Yes |  | Yes |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec | [10 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 300# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 (NACE) | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #300 |  |  | 1" #300 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note4) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-Trim number 12 same as API 602. 5:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-PCV-2101B
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 8 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 6 |  | D-PCV-2101B | [5 empty] | 1
| 2 | Service | [9 empty] | FUEL GAS TO V-120
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 2/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | FLG-111-0030-AN07-1"-PT | [6 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | FUEL GAS |  |  | GAS
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | 127 |  | 127/445 |  |  |  |  | 445 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [9 empty] | 4.9 |  | 4.9 |  |  |  |  | 4.9 |  |  |  |  | barg
| 9 | Outlet Pressure | [9 empty] | 0 |  | 0 / 4.5 |  |  |  |  | 4.5 |  |  |  |  | barg
| 10 | Inlet Temperature | [9 empty] | 45 |  | 48 |  |  |  |  | 50 |  |  |  |  | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 24.52 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 5.74 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 0.01147 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | - |  |  |  |  | -
| 15 | Flash | [9 empty] | - | [6 empty] | -
| 16 | Calculated Cv / Travel | [9 empty] | - | [6 empty] | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.9678 |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.189 |  |  |  |  | -
| 20 | Critical Pres. Pc (Bara) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 104.7 |  | 86.71 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | YES |  | NO |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec |  |  |  | IH | [6 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 300# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 (NACE) | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #300 |  |  | 1" #300 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note4) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note4) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-Trim number 12 same as API 602. 5:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-TCV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 9 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 7 |  | D-TCV-2101 | [5 empty] | 1
| 2 | Service | [9 empty] | FROM FUEL GAS HEADER TO REBOILER
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | FLG-111-0024-AN07-1"-PT | [6 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | Fuel Gas |  |  | Gas
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | 2.5 (4) |  | 10 (4) |  |  |  |  | 13 (4) |  |  |  |  | kg/h
| 8 | Inlet Pressure | [9 empty] | 4.9 |  | 4.9 |  |  |  |  | 4.9 |  |  |  |  | barg
| 9 | Outlet Pressure | [9 empty] | 0.07 (4) |  | 1 (4) |  |  |  |  | 1.5 (4) |  |  |  |  | barg
| 10 | Inlet Temperature | [9 empty] | 15 |  | 19 / 36.78 |  |  |  |  | 48 |  |  |  |  | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 24.52 |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 5.34/5.74 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 0.01/0.01147 |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 4.9 |  |  |  |  | -
| 15 | Flash | [9 empty] | - |  | - |  |  |  |  | -
| 16 | Calculated Cv / Travel | [9 empty] | - |  | - |  |  |  |  | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.9678 |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.189 |  |  |  |  | -
| 20 | Critical Pres. Pc (Bara) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 104.7 |  | 86.71 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | YES |  | NO |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec |  |  |  | IH | [6 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 300# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | *Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | *Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 (NACE) | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #300 |  |  | 1" #300 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note5) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-NNF (Normally No Flow) 5-Trim number 12 same as API 602. 6:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red

## D-LCV-2104
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR CONTROL VALVES
شماره پیمان: |  |  | پروژه | بسته کاری | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  | نسخه |  |  |  | شماره صفحه: 10 از 10
9184 – 073 - 053 |  |  | BK | GCS | MF |  |  | 120 |  |  | IN | DS |  | 0001 |  | V00
GENERAL | 1 | Item Number |  |  | Tag Number |  |  |  | Quantity |  |  | 8 |  | D-LCV-2104 | [5 empty] | 1
| 2 | Service | [9 empty] | FROM E-200 TO C-200
| 3 | P & ID No. |  |  |  | Page No. | [5 empty] | BK-GCS-MF-120-PR-PI-0003 | [6 empty] | 4/7
| 4 | Line No. |  |  |  | Piping Class | [5 empty] | TEG-111-0027-AN07-1"-HI | [6 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  |  | Phase | [5 empty] | TEG |  |  | L/V
| 6 | [10 empty] | Min. Flow |  | Normal. Flow |  |  |  |  | Max. Flow |  |  |  |  | Unit
| 7 | Flow Rate | [9 empty] | 661.52 |  | 826.9 ̴ 834.3 |  |  |  |  | 1001.16 |  |  |  |  | kg/h
| 8 | Inlet Pressure | [9 empty] | 2 |  | 3.1 |  |  |  |  | 4 |  |  |  |  | barg
| 9 | Outlet Pressure | [9 empty] | 1 |  | 1 |  |  |  |  | 1 |  |  |  |  | barg
| 10 | Inlet Temperature | [9 empty] | 120 |  | 140 |  |  |  |  | 160 |  |  |  |  | ˚C
| 11 | Molecular Weight | [9 empty] | - |  | 3.81/4 (vapor) and 103.73/106.54 (liquid) |  |  |  |  | - |  |  |  |  | kg/kmol
| 12 | Density | [9 empty] | - |  | 3.81 / 4 |  |  |  |  | - |  |  |  |  | kg/m3
| 13 | Viscosity | [9 empty] | - |  | 0.014 (vapor) and 1.4113 (liquid) |  |  |  |  | - |  |  |  |  | cp
| 14 | Vapor Pressure Pv | [9 empty] | - |  | 3.1 |  |  |  |  | -
| 15 | Flash | [9 empty] | - |  | - |  |  |  |  | -
| 16 | Calculated Cv / Travel | [9 empty] | - |  | - |  |  |  |  | -
| 17 | Allowable / * Predicted SPL | [9 empty] | 85 |  | 85 |  |  |  |  | 85 |  |  |  |  | dBA
| 18 | Compressibility Factor (Z) | [9 empty] | - |  | 0.9551 (vapor) and 0.01767 (liquid) |  |  |  |  | -
| 19 | Spec. Heat Ratio(K=Cp/Cv) | [9 empty] | - |  | 1.001 |  |  |  |  | -
| 20 | Critical Pres. Pc (Bara) |  |  | Critical Temp. Tc |  | Super Heat |  | Shut-Off Pres. (Bara) |  |  | 31.57 |  | 430.3 |  |  |  |  | -
| 21 | Corrosive Service |  |  | Toxic Service |  | Super Heat |  | Super Heat |  |  | YES |  | YES |  |  |  |  | NO
22
LINE | 23 | Size |  | In | Out | 1" |  |  | 1" |  |  | ACTUATOR | 63 | Type |  |  |  |  | Pneumatic,Spring & Diaphragm
| 24 | Pipe Line Schedule |  | In | Out | XXS |  |  | XXS |  |  |  | 64 | Mfr. & Model |  |  |  |  | VTA
| 25 | Pipe Line Insulation/Spec |  |  |  | IH | [6 empty] | 65 | Size |  | Eff Area |  |  | VTA |  |  | VTA
VALVE BODY / BONNET | 26 | Type |  |  |  | Globe | [6 empty] | 66 | On/Off or Modulated |  | N/A |  |  | Modulated
| 27 | Size |  | ANSI Class |  | 1" |  |  | 300# |  |  |  | 67 | Spring Action Open /Close |  |  |  |  | FC
| 28 | Desing Press. (Bara) |  | Design Temp. (°C) | [8 empty] | 68 | Max Allowable Pressure |  |  |  |  | VTA
| 29 | Mfr. & Model |  |  |  | VTA | [6 empty] | 69 | Min Required Pressure |  |  |  |  | VTA
| 30 | Body / Bonnet Material |  |  |  | ASTM A105 (NACE) | [6 empty] | 70 | Air Supply Pressur |  | Min | Nor | Max | 4 |  | 7.5 |  | 8.5 (NOTE3)
| 31 | Liner Material / ID |  |  |  | VTA | [6 empty] | 71 | *Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 32 | End Connection |  | In | Out | 1" #300 |  |  | 1" #300 |  |  |  | 72 | Act. Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 33 | Flange Face Finish |  |  |  | RF,SW (125-250 AARH) | [6 empty] | 73 | Hand Wheel |  | Limit Stop |  |  | NO |  |  | NO
| 34 | Flow Direction |  |  |  | Bi-Directional(VTA) | [6 empty] | 74 | IP for Pneumatic Parts |  |  | N/A |  | 65
| 35 | Type Of Bonnet |  |  |  | Standard (Bolted) | [6 empty] | 75
| 36 | Packing Material |  | Packing Type |  | Teflon-chevron |  |  | VTA |  |  | POSITIONER | 76 | Type |  |  |  |  | Electro Pneumatic (smart)/Digital-HART
| 37 | Gasket |  |  |  | Spiral Wound,AISI316,Graphite filled,C.S. Outer& S.S316L Inner Ring | [6 empty] | 77 | Mfr. & Model |  |  |  |  | VTA
| 38 | [11 empty] | 78 | Input Signal |  | Output Signal |  |  | 4-20mA |  |  | NO
TRIM | 39 | * Type |  |  |  | (VTA) | [6 empty] | 79 | Action on Increase Signal |  |  |  |  | Increase to Open
| 40 | * Size |  | Rated Travel |  | 1" |  |  | 3/4" |  |  |  | 80 | Cam Characteristics |  |  |  |  | VTA
| 41 | * Characteristics |  |  |  | Equal Precent(VTC) | [6 empty] | 81 | Electrical Connection |  |  |  |  | M20x1.5
| 42 | * Balanced / Unbalanced |  |  |  | Balanced | [6 empty] | 82 | Ex Certificate |  |  |  |  | Zone 2 EX ia IIB T4
| 43 | * Rated Cv |  | Fl | Xt | VTA |  | VTA |  | VTA |  |  | 83 | Ingress Protection |  |  |  |  | 65
| 44 | * Plug / Ball / Disk Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 84 | Housing Material |  |  |  |  | Aluminum Die-cast
| 45 | * Seat Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 85
| 46 | * Cage / Guide Material |  |  |  | SS 316-Hard Face(Note5) | [5 empty] | LIMIT SWITCH | 86 | Type |  | Quantity |  |  | N/A |  |  | N/A
| 47 | * Stem / Material |  |  |  | SS 316-Hard Face(Note5) | [6 empty] | 87 | Mfr. & Model |  |  |  |  | N/A
| 48 | [11 empty] | 88 | Tag Number(s) |  |  |  |  | N/A
SOLENOID VALVE | 49 | Type |  |  |  | N/A | [6 empty] | 89 | Actuation Point |  |  |  |  | N/A
| 50 | Tag Number |  |  |  | N/A | [6 empty] | 90 | Contacts / Rating |  |  |  |  | N/A
| 51 | Body Material |  |  |  | N/A | [6 empty] | 91 | Electrical Connection |  |  |  |  | N/A
| 52 | Operating Voltage |  |  |  | N/A | [6 empty] | 92 | Ex Certificate |  |  |  |  | N/A
| 53 | Elec. Connection |  |  |  | N/A | [6 empty] | 93 | Ingress Protection |  |  |  |  | N/A
| 54 | Manual Reset |  |  |  | N/A | [5 empty] | AIR SET | 94 | Mfr. & Model |  |  |  |  | VTA
| 55 | Ex Certificate |  | Ingress Protection |  | N/A |  |  | N/A |  |  |  | 95 | Set Pressure |  |  |  |  | VTA
| 56 | Pneumatic Connection |  |  |  | N/A | [6 empty] | 96 | Filter |  | Gauges |  |  | YES |  |  | YES
SPECIAL/ ACCESSORIES | 57 | Fusible Leakage |  | Booster |  | IV |  |  | VTA |  |  |  | 97 | Pneumatic Connection |  |  |  |  | 1/4"NPTF(VTA)
| 58 | Block Relay |  | Volume Tank |  | VTA |  |  | NO |  |  | TESTS | 98 | Hydro Pressure |  |  |  |  | YES (ANSI/ASME B16.34)
| 59 | SIL Requiment |  |  |  | NO | [6 empty] | 99 | ANSI / FCI Leakage Class |  |  |  |  | IV
| 60 | [11 empty] | 100 | NACE MR 0175 |  |  |  |  | YES
| 61 | [11 empty] | 101
| 62 | [11 empty] | 102
1-Tubing Material shall be AISI 316L . 2- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable. 3-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg. 4-NNF (Normally No Flow) 5-Trim number 12 same as API 602. 6:The actuator shall be painted as below: Direct acting (open on air failure) – green Reverse acting (close on air failure) – red