## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 12
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0002 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR ON/OFF VALVES نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Apr.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 12
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0002 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 |  | X | [7 empty] | 72
13 | [9 empty] | 73
14 | [9 empty] | 74
15 | [9 empty] | 75
16 | [9 empty] | 76
17 | [9 empty] | 77
18 | [9 empty] | 78
19 | [9 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-ESDV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 3 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 1 |  |  |  | D-ESDV-2101 |  |  |  | 1
| 2 | Service | [5 empty] | C100 TO E100
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 1/7
| 4 | Line No. |  |  | Piping Class |  |  | TEG-111-0001-FN07-1"-HI | [8 empty] | FN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | TEG |  |  |  |  | V / L
| 6 | Toxic Service |  |  | Cold Service |  |  | YES |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 1020 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 52 |  |  |  | 54.9 |  |  |  | 58 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | F.V. / 62 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 62.96 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 5 / 100 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01229 (vapor) and 7.17 (Liquid) | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.002
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 1.082 (liquid phase) and 1.22 (vapor phase)
17
LINE | 18 | Pipe Line Size | In/Out |  | 1" | 1" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | RPTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#600 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#600 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | RPTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 4 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 2 |  |  |  | D-ESDV-2102 |  |  |  | 1
| 2 | Service | [5 empty] | C100 TO HYDROCARBON DRAIN LINE
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 1/7
| 4 | Line No. |  |  | Piping Class |  |  | TEG-111-0027-AN07-1"-HI | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | HCB |  |  |  |  | Liquid
| 6 | Toxic Service |  |  | Cold Service |  |  | YES |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 7 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 52 |  |  |  | 53.9 |  |  |  | 58 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | F.V. / 62 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 59.89 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 5 / 100 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 1 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.165
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 1
17
LINE | 18 | Pipe Line Size | In/Out |  | 1" | 1" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | RPTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#600 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#600 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | RPTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 5 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 3 |  |  |  | D-ESDV-2103 |  |  |  | 1
| 2 | Service | [5 empty] | FROM E200 TO C200
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | TEG-111-0027-AN07-1"-HI | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | TEG |  |  |  |  | V / L
| 6 | Toxic Service |  |  | Cold Service |  |  | YES |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 1000 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 2.5 |  |  |  | 3.1 |  |  |  | 3.8 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | F.V. / 7.5 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 140 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 5 / 165 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01 (vapor) and 1.3908 (liquid) | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.006
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 1.085 (liquid phase) and 1.34 (vapor phase)
17
LINE | 18 | Pipe Line Size | In/Out |  | 1" | 1" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | RPTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | RPTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2104A
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 6 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 4 |  |  |  | D-ESDV-2104A |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0024-AN07-1"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 9.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 4.5 |  |  |  | 4.9 |  |  |  | 5.2 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 1" | 1" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | RPTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | RPTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2104B
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 7 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 5 |  |  |  | D-ESDV-2104B |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0024-AN07-1"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 9.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 4.5 |  |  |  | 4.9 |  |  |  | 5.2 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 1" | 1" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | PTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | PTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2104C
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 8 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 6 |  |  |  | D-ESDV-2104C |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0024-AN07-1"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 9.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 4.5 |  |  |  | 4.9 |  |  |  | 5.2 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 1" | 1" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FO
| 22 | Size |  |  | 1" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | PTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | PTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2105A
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 9 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 7 |  |  |  | D-ESDV-2105A |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0026-AN07-1/2"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 9.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 0.1 |  |  |  | 0.5 |  |  |  | 1 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 1/2" | 1/2" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1/2" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | PTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1/2"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1/2"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | PTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2105B
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 10 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 8 |  |  |  | D-ESDV-2105B |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0026-AN07-1/2"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 9.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 0.1 |  |  |  | 0.5 |  |  |  | 1 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 1/2" | 1/2" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 1/2" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | PTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1/2"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1/2"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | PTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2105C
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 11 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 9 |  |  |  | D-ESDV-2105C |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0026-AN07-1/2"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 9.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 0.1 |  |  |  | 0.5 |  |  |  | 1 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 1/2" | 1/2" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH.XXS | SCH.XXS |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FO
| 22 | Size |  |  | 1/2" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | PTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | ASTM A105 |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 1"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 1"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. SW |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | PTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | anti-blow out (VTA) |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.

## D-ESDV-2106
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR ON/OFF VALVES
شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده |  |  | تسهیلات |  |  | رشته | نوع مدرک |  | سریال |  |  | نسخه |  | شماره صفحه: 12 از 12
9184 – 073 - 053 |  |  | BK | GCS |  | MF |  |  | 120 |  |  | IN | DS |  | 0002 |  |  | V00
GENERAL | 1 | Item Number |  | Tag Number |  | Quantity |  | 10 |  |  |  | D-ESDV-2106 |  |  |  | 1
| 2 | Service | [5 empty] | FROM HEADER GAS TO REBOILER / SURGE FRUM
| 3 | P & ID No. |  |  | Page No. |  |  | BK-GCS-MF-120-PR-PI-0003 | [8 empty] | 5/7
| 4 | Line No. |  |  | Piping Class |  |  | FLG-111-0027-AN07-2"-PT | [8 empty] | AN07
PROCESS CONDITIONS | 5 | Fluid |  |  | Phase |  |  | FUEL GAS |  |  |  |  | GAS
| 6 | Toxic Service |  |  | Cold Service |  |  | NO |  |  |  |  | NO
| 7 | Corrosive Service |  |  | Errossive Service |  |  | YES |  |  |  |  | -
| 8 | Max. Flow Rate |  |  |  |  | Unit | 69.3 | [11 empty] | kg/h
| 9 | Operating Pressure |  | Min. | Normal | Max | Unit | 4.5 |  |  |  | 4.9 |  |  |  | 5.2 |  |  |  | barg
| 10 | Max. Diff. Pressure for Actuator Size |  |  |  |  | Unit | -
| 11 | Design Pressure |  |  |  |  | Unit | 9 | [11 empty] | barg
| 12 | Operating Temperature |  |  |  |  | Unit | 19/36.78 | [11 empty] | ˚C
| 13 | Design Temperature |  |  |  |  | Unit | 85 | [11 empty] | ˚C
| 14 | Viscosity |  |  |  |  | Unit | 0.01147 | [11 empty] | cp
| 15 | Spec. Heat Ratio(K=Cp/Cv) | [5 empty] | 1.228
| 16 | Spec. Wt./Spec.Grav./Mol Wt | [5 empty] | 0.8487
17
LINE | 18 | Pipe Line Size | In/Out |  | 2" | 2" |  | ACTUATOR |  | 61 | Type |  |  |  |  | single acting, spring return pneumatic actuators
| 19 | Schedule | In/Out |  | SCH160 | SCH160 |  |  |  | 62 | Mfr. & Model |  |  |  |  | VTA
| 20 | Pipe Line Insulation |  |  | - |  |  |  |  | 63 | Size |  |  | Eff Area |  | VTA |  |  | VTA
VALVE BODY / BONNET | 21 | Type |  |  | Ball (top entry) |  |  |  |  | 64 | Action on Air Failure |  |  |  |  | FC
| 22 | Size |  |  | 2" |  |  |  |  | 65 | Max Allowable Pressure |  |  |  |  | VTA
| 23 | Mfr. & Model |  |  | VTA |  |  |  |  | 66 | Min Required Pressure |  |  |  |  | VTA
| 24 | Seal Material |  |  | PTFE |  |  |  |  | 67 | Available Air Supply Pressure |  |  |  |  | 4 - 8.5 barg (NOTE7)
| 25 | Body / Bonnet Material |  |  | A216 Gr.WCB |  |  |  |  | 68 | Nor. Air Supply Pres.(barg) |  |  |  |  | 7.5 barg (NOTE7)
| 26 | Flow Direction |  |  | Bi-directional |  |  |  |  | 69 | Bench Range |  |  |  |  | 0.2-1 barg(VTC)
| 27 | Liner Material / ID |  |  | VTA |  |  |  |  | 70 | Actuator Orientation |  |  |  |  | Top, Horizontal, Parallel(VTC)
| 28 | End Connection | In |  | 2"#300 |  |  |  |  | 71 | Hand Wheel |  |  |  |  | No
| 29 |  | Out |  | 2"#300 |  |  |  |  | 72 | Air Failure Valve |  |  | Set At |  | N/A |  |  | N/A
| 30 | Flange Face Finish |  |  | RF. WN (125-250 AARH) |  |  |  |  | 73 | Limit Stop |  |  |  |  | NO
| 31 | Type Of Bonnet |  |  | Standard (Bolted) |  |  |  |  | 74 | Air Consumption |  |  |  |  | VTA
| 32 | Lube & ISO Valve |  |  | VTA |  |  |  |  | 75 | Travel Indicator |  |  |  |  | YES
| 33 | Packing Material/TYPE |  |  | Teflon-chevron/VTA |  |  |  |  | 76 | Pneumatic Connection |  |  |  |  | 1/4” NPTF(VTC)
| 34 | GASKET |  |  | AISI316,Graphite filled |  |  |  |  | 77 | Fire Proof |  |  |  |  | NO
| 35 | Bolt/Nut |  |  | Stud bolt: ASTM A 193-B7M nut: ASTM A 194 -2HM ASME B18.2 |  |  |  |  | 78 | Stroke Time (s) |  |  | Time (s) to Open |  | Sec <5
| 36 | [8 empty] | 79 |  |  |  | Time (s) to Close |  | Sec <3
| 37 | Fire Safe / Antistatic |  |  | Yes / Yes |  |  |  |  | 80 | Ingress Protection |  |  |  |  | 65
| 38 | Hand wheel |  |  | No |  |  |  |  | 81 | Air set Prss. (Min) |  |  |  |  | 4 barg(VTC)
TRIM | 39 | Type | FB/RB |  | Trunnion | FB |  | LIMIT SWITCH |  | 82 | Type |  |  |  |  | Proximity type
| 40 | Plug / Ball / Disk Material |  |  | SS316 |  |  |  |  | 83 | Mfr. & Model |  |  |  |  | VTA
| 41 | Seat Material |  |  | HARDENED SS/STELLITED |  |  |  |  | 84 | Contacts / Rating |  |  |  |  | 24VDC
| 42 | Seal Material |  |  | PTFE |  |  |  |  | 85 | Electrical Connection |  |  |  |  | M20x1.5
| 43 | Stem Material |  |  | SS316 |  |  |  |  | 86 | Ex Certificate |  |  |  |  | EX d IIB T4
| 44 | Leakage Class |  |  | Tight Shut-off/VI (ANSI B 16.104) |  |  |  |  | 87 | Weather Protection |  |  |  |  | 65
| 45 | Stem Type |  |  | VTA |  |  |  |  | 88 | Material |  |  |  |  | Aluminum Die-Cast
SOLENOID VALVE | 46 | DCS Operated SOV |  |  | N/A |  |  |  |  | 89
| 47 | ESD Operated SOV |  |  | ESD/BMS |  |  | SPECIAL / ACCESSORIES |  | 90 | Local Partial Stroke |  |  |  |  | YES
| 48 | Body Material |  |  | SS316 |  |  |  |  | 91 | Volume Tank |  |  |  |  | NO
| 49 | Operating Voltage |  |  | 24VDC |  |  |  |  | 92 | NACE MR 0175 |  |  |  |  | YES
| 50 | Elec. Connection |  |  | M20x1.5 |  |  |  |  | 93 | Material Certificate |  |  |  |  | YES
| 51 | Pneumatic Connection |  |  | VTA |  |  |  |  | 94 | Quick Exhaust |  |  |  |  | VTA
| 52 | Ex Certificate |  |  | EX d IIB T4 |  |  |  |  | 95 | SIL Requiment |  |  |  |  | To be specified by the client
| 53 | Ingress Protection |  |  | IP65 |  |  |  |  | 96 | Valve Typical No. |  |  |  |  | NO
| 54 | Manual Reset |  |  | NO |  |  |  |  | 97 | Positioner |  |  |  |  | NO
| 55 | Mfr. & Model |  |  | VTA |  |  |  |  | 98 | Other |  |  |  |  | NO
| 56 | Type |  |  | Three -way |  |  | TESTS |  | 99 | Hydro Pressure |  |  |  |  | YES
AIR SET | 57 | Mfr. & Model |  |  | VTA |  |  |  |  | 100 | ANSI / FCI Leakage Class |  |  |  |  | YES
| 58 | Set Press. |  |  | 7.5barg |  |  |  |  | 101 | Other |  |  |  |  | VTA
| 59 | Filter | Gauge |  | YES |  | YES |  |  | 102
| 60 | Material |  |  | Aluminum Die-Cast |  |  | PURCHASE |  | 103
Notes 1- VTA:Vendor to Advise VTC:Vendor to Confirm N/A:Not Applicable 2- The actuator shall be sized using a thrust/torque safety factor at least of 1.3 times. 3- All pneumatic operated ON-OFF valves assembly shall be provided with a permanently fastened tag plate of SS316. 4- The final external pneumatic connection shall be 1/2"NPTF, internal connections are 1/4", accessories shall be supplied by vendor. 5-All valves test shall be in accordance with API 6D & API 598 6- The material of all valves will be in accordance with the project PMS(BK-GCS-PEDCO-120-PI-SP-0001_D02). 7-Actuators shall be sized for a minimum air pressure of 3 barg. The normal operating pressure is 4 barg, and the maximum operating pressure is 10 barg and shall be tested at 1.5 times of the maximum air supply.