## Cover
NISOC |  |  |  | نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
| شماره پیمان: |  |  | پروژه |  | بسته کاری | صادرکننده | تسهیلات |  | رشته | نوع مدرک | سریال | نسخه |  | شماره صفحه: 1 از 19
| 9184 – 073 - 053 |  |  | BK |  | GCS | MF | 120 |  | IN | DS | 0013 | V00
طرح نگهداشت و افزایش تولید 27 مخزن
INSTRUMENT D.S. FOR SAFETY VALVES نگهداشت و افزایش تولید میدان نفتی بینک
| V00 |  | Apr.2025 |  | IFA |  |  |  | MFS |  |  | M.Fakharian |  | S.Faramarzpour
| Rev. |  | Date |  | Purpose of Issue / Status |  |  |  | Prepared by: |  |  | Checked by: |  | Approved by: |  | CLIENT Approval
[5 empty] | CLIENT Doc. Number: |  |  |  | -
status:
IFA: Issued For Approval
IFI: Issued For Information
AFC: Approved For Construction

## REVISION
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
| شماره پیمان: |  |  | پروژه | بسته کاری |  | صادرکننده | تسهیلات | رشته | نوع مدرک | سریال |  | نسخه |  | شماره صفحه: 2 از 19
| 9184 – 073 - 053 |  |  | BK | GCS |  | MF | 120 | IN | DS | 0013 |  | V00
REVISION RECORD SHEET
Page |  | V00 | V01 | V02 |  | V03 |  | V04 |  | Page |  | V00 |  | V01 |  | V02 | V03 | V04
1 |  | X | [7 empty] | 61
2 |  | X | [7 empty] | 62
3 |  | X | [7 empty] | 63
4 |  | X | [7 empty] | 64
5 |  | X | [7 empty] | 65
6 |  | X | [7 empty] | 66
7 |  | X | [7 empty] | 67
8 |  | X | [7 empty] | 68
9 |  | X | [7 empty] | 69
10 |  | X | [7 empty] | 70
11 |  | X | [7 empty] | 71
12 |  | X | [7 empty] | 72
13 |  | X | [7 empty] | 73
14 |  | X | [7 empty] | 74
15 |  | X | [7 empty] | 75
16 |  | X | [7 empty] | 76
17 |  | X | [7 empty] | 77
18 |  | X | [7 empty] | 78
19 |  | X | [7 empty] | 79
20 | [9 empty] | 80
21 | [9 empty] | 81
22 | [9 empty] | 82
23 | [9 empty] | 83
24 | [9 empty] | 84
25 | [9 empty] | 85
26 | [9 empty] | 86
27 | [9 empty] | 87
28 | [9 empty] | 88
29 | [9 empty] | 89
30 | [9 empty] | 90
31 | [9 empty] | 91
32 | [9 empty] | 92
33 | [9 empty] | 93
34 | [9 empty] | 94
35 | [9 empty] | 95
36 | [9 empty] | 96
37 | [9 empty] | 97
38 | [9 empty] | 98
39 | [9 empty] | 99
40 | [9 empty] | 100
41 | [9 empty] | 101
42 | [9 empty] | 102
43 | [9 empty] | 103
44 | [9 empty] | 104
45 | [9 empty] | 105
46 | [9 empty] | 106
47 | [9 empty] | 107
48 | [9 empty] | 108
49 | [9 empty] | 109
50 | [9 empty] | 110
51 | [9 empty] | 111
52 | [9 empty] | 112
53 | [9 empty] | 113
54 | [9 empty] | 114
55 | [9 empty] | 115
56 | [9 empty] | 116
57 | [9 empty] | 117
58 | [9 empty] | 118
59 | [9 empty] | 119
60 | [9 empty] | 120

## D-PSV-2101
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 3 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2101
| 2 | Service | [7 empty] | FROM C-100
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 1/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | GAS-111-0001-FN07-2"-PT | [5 empty] | FN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | GAS |  |  |  | V
| 12 | Required Capacity | [5 empty] | Unit |  | 9655 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 0.80929
| 14 | Molecular Weight | [7 empty] | 22.66
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 54 |  |  | 62 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 63.5 |  |  | 382.9 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | 0.2 | [7 empty] | barg
| 18 |  |  |  | Variable |  |  | Unit |  | 1.393 | [7 empty] | barg
| 19 |  |  |  | Total |  |  | Unit |  | 1.593 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Flare
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 21% |  |  |  | 1.21
| 22 | Compressibility Factor (Z) | [7 empty] | 0.7435
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | 116.5 | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | 1.688
| 25 | Relief Density | [5 empty] | Unit |  | 49.02 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 0.7435 (liquid) / 0.08896 (vapor) | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26 / 14.37 psia
| 28 | Blowdown | [7 empty] | 0.2 bar
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | FIRE
| 33 | Calculated Area | [7 empty] | 0.446 in2 ( 287.74mm2)
| 34 | Selected Area | [7 empty] | 0.503 in2 ( 324.52 mm2)
| 35 | Orifice Designation | [7 empty] | G
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1 1/2" |  |  |  | 3"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 600# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disk |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT& NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2102
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 4 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2102
| 2 | Service | [7 empty] | FROM C-100
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 1/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | GAS-111-0001-FN07-2"-PT | [5 empty] | FN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | GAS |  |  |  | V
| 12 | Required Capacity | [5 empty] | Unit |  | 9655 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 0.80929
| 14 | Molecular Weight | [7 empty] | 22.66
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 54 |  |  | 62 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 63.5 |  |  | 382.9 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | 0.2 | [7 empty] | barg
| 18 |  |  |  | Variable |  |  | Unit |  | 1.393 | [7 empty] | barg
| 19 |  |  |  | Total |  |  | Unit |  | 1.593 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Flare
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 21% |  |  |  | 1.21
| 22 | Compressibility Factor (Z) | [7 empty] | 0.7435
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | 116.5 | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | 1.688
| 25 | Relief Density | [5 empty] | Unit |  | 49.02 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 0.7435 (liquid) / 0.08896 (vapor) | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26 / 14.37 psia
| 28 | Blowdown | [7 empty] | 0.2 bar
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | FIRE
| 33 | Calculated Area | [7 empty] | 0.446 in2 ( 287.74mm2)
| 34 | Selected Area | [7 empty] | 0.503 in2 ( 324.52 mm2)
| 35 | Orifice Designation | [7 empty] | G
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1 1/2" |  |  |  | 3"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 600# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2103
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 5 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2103
| 2 | Service | [7 empty] | FROM V-120
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 2/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | GAS-111-0002-AN07-2"-PP | [5 empty] | AN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | GAS |  |  |  | V
| 12 | Required Capacity | [5 empty] | Unit |  | 5384 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.0482
| 14 | Molecular Weight | [7 empty] | 29.35
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 4.5 |  |  | 8 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 74 |  |  | 201.2 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | 0.2 | [7 empty] | barg
| 18 |  |  |  | Variable |  |  | Unit |  | 1.393 | [7 empty] | barg
| 19 |  |  |  | Total |  |  | Unit |  | 1.593 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Flare
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 21% |  |  |  | 1.21
| 22 | Compressibility Factor (Z) | [7 empty] | 0.9679
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | 248.5 | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | 1.233
| 25 | Relief Density | [5 empty] | Unit |  | 8.17 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 0.016116
| 27 | Barometric Pressure | [7 empty] | 13.26 - 14.37 psia
| 28 | Blowdown | [7 empty] | 0.58
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | FIRE
| 33 | Calculated Area | [7 empty] | 1.11 in2 (716.13 mm2)
| 34 | Selected Area | [7 empty] | 1.287 in2 ( 830.32mm2)
| 35 | Orifice Designation | [7 empty] | J
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 3" |  |  |  | 4"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2104
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 6 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2104
| 2 | Service | [7 empty] | FROM V-120
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 2/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | GAS-111-0002-AN07-2"-PP | [5 empty] | AN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | GAS |  |  |  | V
| 12 | Required Capacity | [5 empty] | Unit |  | 5384 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.0482
| 14 | Molecular Weight | [7 empty] | 29.35
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 4.5 |  |  | 8 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 74 |  |  | 201.2 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | 0.2 | [7 empty] | barg
| 18 |  |  |  | Variable |  |  | Unit |  | 1.393 | [7 empty] | barg
| 19 |  |  |  | Total |  |  | Unit |  | 1.593 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Flare
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 21% |  |  |  | 1.21
| 22 | Compressibility Factor (Z) | [7 empty] | 0.9679
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | 248.5 | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | 1.233
| 25 | Relief Density | [5 empty] | Unit |  | 8.17 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 0.016116
| 27 | Barometric Pressure | [7 empty] | 13.26 - 14.37 psia
| 28 | Blowdown | [7 empty] | 0.58
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | FIRE
| 33 | Calculated Area | [7 empty] | 1.11 in2 (716.13 mm2)
| 34 | Selected Area | [7 empty] | 1.287 in2 ( 830.32mm2)
| 35 | Orifice Designation | [7 empty] | J
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 3" |  |  |  | 4"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2105
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 7 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2105
| 2 | Service | [7 empty] | FROM F-100-A
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 3/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | TEG-111-0011-AN07-1"-HI | [5 empty] | AN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.071
| 14 | Molecular Weight | [7 empty] | 101.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 4.5 |  |  | 8 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 73.6 |  |  | 85 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 1071 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 5.472 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.047 in2 (30.32 mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2106
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 8 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2106
| 2 | Service | [7 empty] | FROM F-100-B
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 3/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | TEG-111-0012-AN07-1"-HI | [5 empty] | AN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.071
| 14 | Molecular Weight | [7 empty] | 101.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 4.5 |  |  | 8 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 73.6 |  |  | 85 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 1071 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 5.472 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.047 in2 (30.32 mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2107
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 9 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2107
| 2 | Service | [7 empty] | FROM F-200-A
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 3/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | VTEG-111-0019-AN07-1"-HI | [5 empty] | AN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.061
| 14 | Molecular Weight | [7 empty] | 101.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 3.8 |  |  | 7.5 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 73.6 |  |  | 85 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 1061 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 5.472 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.049 in2 ( 31.61mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2108
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 10 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2108
| 2 | Service | [7 empty] | FROM F-200-B
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 3/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | TEG-111-0018-AN07-1"-HI | [5 empty] | AN07
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.061
| 14 | Molecular Weight | [7 empty] | 101.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 3.8 |  |  | 7.5 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 73.6 |  |  | 85 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 1061 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 5.472 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.049 in2 ( 31.61mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2109
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 11 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2109
| 2 | Service | [7 empty] | FROM R-100
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | GAS-111-0004-AN05-6"-HI | [5 empty] | AN05
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | GAS |  |  |  | V
| 12 | Required Capacity | [5 empty] | Unit |  | 14690 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 2.2707
| 14 | Molecular Weight | [7 empty] | 63.58
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 0.3/0.5 |  |  | 4.1 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 140/204 |  |  | 316.4 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | 0.2 | [7 empty] | barg
| 18 |  |  |  | Variable |  |  | Unit |  | 1.393 | [7 empty] | barg
| 19 |  |  |  | Total |  |  | Unit |  | 1.593 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Flare
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 21% |  |  |  | 1.21
| 22 | Compressibility Factor (Z) | [7 empty] | 0.9210
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | 242 | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | 1.074
| 25 | Relief Density | [5 empty] | Unit |  | 8.137 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 0.012519 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | 0.9
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | FIRE
| 33 | Calculated Area | [7 empty] | 6.328 in2 ( 4082.57 mm2)
| 34 | Selected Area | [7 empty] | 6.38 in2 ( 4116.12 mm2)
| 35 | Orifice Designation | [7 empty] | P
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 4" |  |  |  | 6"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2110
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 12 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2110
| 2 | Service | [7 empty] | FROM R-100
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 4/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | GAS-111-0004-AN05-6"-HI | [5 empty] | AN05
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | GAS |  |  |  | V
| 12 | Required Capacity | [5 empty] | Unit |  | 14690 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 2.2707
| 14 | Molecular Weight | [7 empty] | 63.58
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 0.3/0.5 |  |  | 4.1 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 140/204 |  |  | 316.4 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | 0.2 | [7 empty] | barg
| 18 |  |  |  | Variable |  |  | Unit |  | 1.393 | [7 empty] | barg
| 19 |  |  |  | Total |  |  | Unit |  | 1.593 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Flare
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 21% |  |  |  | 1.21
| 22 | Compressibility Factor (Z) | [7 empty] | 0.9210
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | 242 | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | 1.074
| 25 | Relief Density | [5 empty] | Unit |  | 8.137 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 0.012519 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | 0.9
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | FIRE
| 33 | Calculated Area | [7 empty] | 6.328 in2 ( 4082.57 mm2)
| 34 | Selected Area | [7 empty] | 6.38 in2 ( 4116.12 mm2)
| 35 | Orifice Designation | [7 empty] | P
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 4" |  |  |  | 6"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | YES
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2111
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 13 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2111
| 2 | Service | [7 empty] | FROM E-200
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 5/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | TEG-111-0003-AN04-1"-HI | [5 empty] | AN04
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | V/L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 0.9329
| 14 | Molecular Weight | [7 empty] | 147.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 55 |  |  | 62 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 120 |  |  | 130 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 932.9 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 1.409(Liquid Phase) / 0.01405 (Vapor Phase) | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.044 in2 ( 28.39 mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | NO
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2112
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 14 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2112
| 2 | Service | [7 empty] | FROM P-100-A
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 5/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | TEG-111-0004-AN04-1"-HI | [5 empty] | AN04
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.054
| 14 | Molecular Weight | [7 empty] | 147.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 55.1 |  |  | 62 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 120 |  |  | 130 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 1054 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 2.377 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.044 in2 ( 28.39 mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | NO
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2113
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 15 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2113
| 2 | Service | [7 empty] | FROM P-100-B
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 5/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | TEG-111-0005-AN04-1"-HI | [5 empty] | AN04
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | TEG |  |  |  | L
| 12 | Required Capacity | [5 empty] | Unit |  | 834.3 | [7 empty] | kg/h
| 13 | Operating Sp. Gr. | [7 empty] | 1.054
| 14 | Molecular Weight | [7 empty] | 147.8
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | 55.1 |  |  | 62 |  |  |  |  | barg
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | 120 |  |  | 130 |  |  |  |  | C
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | -
| 18 |  |  |  | Variable |  |  | Unit |  | -
| 19 |  |  |  | Total |  |  | Unit |  | 3.5 | [7 empty] | barg
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Glycol Drain Vessel
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | 10% |  |  |  | 1.1
| 22 | Compressibility Factor (Z) | [7 empty] | -
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | - | [7 empty] | kj/kg
| 24 | Ratio of Specific Heats | [7 empty] | -
| 25 | Relief Density | [5 empty] | Unit |  | 1054 | [7 empty] | kg/m3
| 26 | Relief Viscosity | [5 empty] | Unit |  | 2.377 | [7 empty] | cp
| 27 | Barometric Pressure | [7 empty] | 13.26/14.37 psia
| 28 | Blowdown | [7 empty] | -
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | -
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | YES |  |  |  | YES
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Thermal Expansion
| 33 | Calculated Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 34 | Selected Area | [7 empty] | 0.110 in2 ( 70.97mm2)
| 35 | Orifice Designation | [7 empty] | D
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | NO
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57

## D-PSV-2114
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 16 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2114
| 2 | Service | [7 empty] | FROM P-200-A
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 6/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | CHM-111-0005-AS00-1"-HI | [5 empty] | AS00
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 12 | Required Capacity | [5 empty] | Unit |  | Will be finalized later
| 13 | Operating Sp. Gr. | [7 empty] | Will be finalized later
| 14 | Molecular Weight | [7 empty] | Will be finalized later
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | Will be finalized later
| 18 |  |  |  | Variable |  |  | Unit |  | Will be finalized later
| 19 |  |  |  | Total |  |  | Unit |  | Will be finalized later
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Will be finalized later
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 22 | Compressibility Factor (Z) | [7 empty] | Will be finalized later
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | Will be finalized later
| 24 | Ratio of Specific Heats | [7 empty] | Will be finalized later
| 25 | Relief Density | [5 empty] | Unit |  | Will be finalized later
| 26 | Relief Viscosity | [5 empty] | Unit |  | Will be finalized later
| 27 | Barometric Pressure | [7 empty] | Will be finalized later
| 28 | Blowdown | [7 empty] | Will be finalized later
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | Will be finalized later
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Blocked Outlet
| 33 | Calculated Area | [7 empty] | in2 ( mm2)
| 34 | Selected Area | [7 empty] | in2 ( mm2)
| 35 | Orifice Designation
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | Yes
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57
THIS PSV WILL BE FINALIZED AFTER RECEIVING VENDOR DATA

## D-PSV-2115
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 17 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2115
| 2 | Service | [7 empty] | FROM P-200-B
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 6/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | CHM-111-0005-AS00-1"-HI | [5 empty] | AS00
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 12 | Required Capacity | [5 empty] | Unit |  | Will be finalized later
| 13 | Operating Sp. Gr. | [7 empty] | Will be finalized later
| 14 | Molecular Weight | [7 empty] | Will be finalized later
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | Will be finalized later
| 18 |  |  |  | Variable |  |  | Unit |  | Will be finalized later
| 19 |  |  |  | Total |  |  | Unit |  | Will be finalized later
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Will be finalized later
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 22 | Compressibility Factor (Z) | [7 empty] | Will be finalized later
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | Will be finalized later
| 24 | Ratio of Specific Heats | [7 empty] | Will be finalized later
| 25 | Relief Density | [5 empty] | Unit |  | Will be finalized later
| 26 | Relief Viscosity | [5 empty] | Unit |  | Will be finalized later
| 27 | Barometric Pressure | [7 empty] | Will be finalized later
| 28 | Blowdown | [7 empty] | Will be finalized later
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | Will be finalized later
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Blocked Outlet
| 33 | Calculated Area | [7 empty] | in2 ( mm2)
| 34 | Selected Area | [7 empty] | in2 ( mm2)
| 35 | Orifice Designation
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | Yes
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57
THIS PSV WILL BE FINALIZED AFTER RECEIVING VENDOR DATA

## D-PSV-2116
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 18 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2116
| 2 | Service | [7 empty] | FROM P-300-A
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 7/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | CHM-111-0006-AS00-1"-HI | [5 empty] | AS00
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 12 | Required Capacity | [5 empty] | Unit |  | Will be finalized later
| 13 | Operating Sp. Gr. | [7 empty] | Will be finalized later
| 14 | Molecular Weight | [7 empty] | Will be finalized later
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | Will be finalized later
| 18 |  |  |  | Variable |  |  | Unit |  | Will be finalized later
| 19 |  |  |  | Total |  |  | Unit |  | Will be finalized later
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Will be finalized later
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 22 | Compressibility Factor (Z) | [7 empty] | Will be finalized later
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | Will be finalized later
| 24 | Ratio of Specific Heats | [7 empty] | Will be finalized later
| 25 | Relief Density | [5 empty] | Unit |  | Will be finalized later
| 26 | Relief Viscosity | [5 empty] | Unit |  | Will be finalized later
| 27 | Barometric Pressure | [7 empty] | Will be finalized later
| 28 | Blowdown | [7 empty] | Will be finalized later
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | Will be finalized later
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Blocked Outlet
| 33 | Calculated Area | [7 empty] | in2 ( mm2)
| 34 | Selected Area | [7 empty] | in2 ( mm2)
| 35 | Orifice Designation
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | Yes
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57
THIS PSV WILL BE FINALIZED AFTER RECEIVING VENDOR DATA

## D-PSV-2117
نگهداشت و افزایش تولید میدان نفتی بینک سطح الارض و ابنیه تحت الارض خرید بسته نم زدای گاز ایستگاه تقویت فشار گاز بینک (قرارداد BK-HD-GCS-CO-0010_08 )
INSTRUMENT D.S. FOR SAFETY VALVES
شماره پیمان: |  |  |  | پروژه | بسته کاری | صادرکننده | تسهیلات |  | رشته |  | نوع مدرک |  | سریال |  | نسخه |  | شماره صفحه: 19 از 19
9184 – 073 - 053 |  |  |  | BK | GCS | MF | 120 |  | IN |  | DS |  | 0013 |  | V00
GENERAL | 1 | Tag Number | [7 empty] | D-PSV-2117
| 2 | Service | [7 empty] | FROM P-300-B
| 3 | P & ID No. |  |  | Page No. |  |  |  |  | BK-GCS-MF-120-PR-PI-0003 | [5 empty] | 7/7
| 4 | Line No. |  |  | Piping Class |  |  |  |  | CHM-111-0006-AS00-1"-HI | [5 empty] | AS00
VALVE DESIGN | 5 | Nozzle : |  | Full, Semi | [5 empty] | Full
| 6 | Design : |  | Safety, Relief, Safety-Relief | [5 empty] | Safety-Relief
| 7 | Type : |  | Conventional, Bellows, Pilot Operated | [5 empty] | Conventional
| 8 | Bonnet Type : |  | Open, Closed | [5 empty] | Closed
| 9 | Seat Type : |  | Metal to Metal, Resilient | [5 empty] | Metal to Metal
| 10 | Seat Tightness : |  | API 527, Other | [5 empty] | API-527
PROCESS CONDITIONS | 11 | Fluid |  |  | Phase |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 12 | Required Capacity | [5 empty] | Unit |  | Will be finalized later
| 13 | Operating Sp. Gr. | [7 empty] | Will be finalized later
| 14 | Molecular Weight | [7 empty] | Will be finalized later
| 15 | Oper. Pressure |  |  | Set Pressure |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 16 | Oper. Temperature |  |  | Relieving Temp. |  |  | Unit |  | Will be finalized later |  |  | Will be finalized later
| 17 | Back Pressure |  |  | Constant |  |  | Unit |  | Will be finalized later
| 18 |  |  |  | Variable |  |  | Unit |  | Will be finalized later
| 19 |  |  |  | Total |  |  | Unit |  | Will be finalized later
| 20 | Discharge to |  |  | Flare /Atm./ Other |  |  |  |  | Will be finalized later
| 21 | % Allowable Overpressure |  |  | Overpressure Factor |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
| 22 | Compressibility Factor (Z) | [7 empty] | Will be finalized later
| 23 | Latent Heat of Vaporization | [5 empty] | Unit |  | Will be finalized later
| 24 | Ratio of Specific Heats | [7 empty] | Will be finalized later
| 25 | Relief Density | [5 empty] | Unit |  | Will be finalized later
| 26 | Relief Viscosity | [5 empty] | Unit |  | Will be finalized later
| 27 | Barometric Pressure | [7 empty] | Will be finalized later
| 28 | Blowdown | [7 empty] | Will be finalized later
| 29 | Cold Differential Test Pressure | [5 empty] | Unit |  | Will be finalized later
| 30 | Corrosive Service |  |  | Toxic Service |  |  |  |  | Will be finalized later |  |  |  | Will be finalized later
BASIS AND SELECTION | 31 | Design Code |  |  | Stamp Required |  |  |  |  | API-520/526
| 32 | Sizing Basis | [7 empty] | Blocked Outlet
| 33 | Calculated Area | [7 empty] | in2 ( mm2)
| 34 | Selected Area | [7 empty] | in2 ( mm2)
| 35 | Orifice Designation
36
CONNECTIONS | 37 | Size/Sch. : Inlet |  |  | Outlet |  |  |  |  | 1" |  |  |  | 2"
| 38 | Rating | Inlet | Outlet | Facing |  |  |  |  | 300# |  | 150# |  | RF
| 39 | Flange Face Finish | [7 empty] | 125 to 250 µin Ra
| 40 | Flange Std. | [7 empty] | ASME B16.5
MATERIALS | 41 | Body and Bonnet |  |  | Nozzle & Disc (Note 1) |  |  |  |  | ASTM A105 |  |  |  | SS316
| 42 | Seat and Rings | [7 empty] | SS316
| 43 | Resilient Seat Seal | [7 empty] | N/A
| 44 | Guide and Rings | [7 empty] | SS 316
| 45 | Spring | [7 empty] | SS 316
| 46 | Bellows | [7 empty] | N/A
| 47 | Bolting
| 48 | Comply with NACE MR 0175 | [7 empty] | Yes
ACCESSORIES | 49 | Cap: Screwed or Bolted | [7 empty] | Screwed
| 50 | Lever: Plain or Packed | [7 empty] | Packed
| 51 | Test Gag | [7 empty] | Yes
| 52 | Bug Screen | [7 empty] | No
| 53 | Other | [7 empty] | INLET BOLT&NUT
PURCHASE | 54 | Manufacturer | [7 empty] | Will be finalized later
| 55 | Model | [7 empty] | Will be finalized later
| 56 | Requisition Number | [7 empty] | Will be finalized later
57
THIS PSV WILL BE FINALIZED AFTER RECEIVING VENDOR DATA